## sheet1
NO. | Redundant | TAG NAME | P&ID | DESCRIPTION | FUN SYS | POWER SUPPLY | SIG TYPE | SENSOR TYPE | UNIT | LOW LIMIT | HI LIMIT | REMARK | MODULE | CH
438 | 1 | 10LBQ10CP101 | J0202-03 | 1段抽汽压力NO.1EXTRACTIONSTEAMPRESSURE | DAS | S | AI | 4~20mA | MPa | 0 | 10 |  | 0 | 1
507 | 1 | 10LBR10AA001XQ01 | J0202-03 | 小机A排汽阀阀位反馈BFPTAEXHAUSTSTEAMVALVEPOSITION | SCS | S | AI | 4~20mA |  |  |  |  | 0 | 2
543 | 1 | 10LBR40CF101 | J0202-03 | 4段抽汽至小机流量1NO.4EXTRACTIONSTEAMTOBFPTURBINESFLOW1 | DAS | S | AI | 4~20mA | t/h | 0 | 44.291 |  | 0 | 3
612 | 1 | 10LBS40CP102 | J0202-03 | 4段抽汽至除氧器压力1NO.4EXTRACTIONSTEAMTODEAERATORSTEAMPRESSURE1 | SCS | S | AI | 4~20mA | MPa | 0 | 1.2 |  | 0 | 4
677 |  | 10LBS60CP101 | J0202-03 | 6段抽汽压力NO.6EXTRACTIONSTEAMPRESSURE | DAS | S | AI | 4~20mA | MPa | 0 | 0.4 |  | 0 | 5
646 |  | 10LBS50CP101 | J0202-03 | 5段抽汽压力NO.5EXTRACTIONSTEAMPRESSURE | DAS | S | AI | 4~20mA | MPa | 0 | 0.8 |  | 0 | 6
611 |  | 10LBS40CP101 | J0202-03 | 4段抽汽压力NO.4EXTRACTIONSTEAMPRESSURE | DAS | S | AI | 4~20mA | MPa | 0 | 1.2 |  | 0 | 7
610 |  | 10LBS40CF101 | J0202-03 | 4段抽汽至辅汽流量NO.4EXTRACTIONSTEAMTOAUXILIARYSTEAMFLOW | DAS | S | AI | 4~20mA | t/h | 0 | 50 |  | 0 | 8
123 |  | 10LBC10CP102 | J0202-01 | 冷再热蒸汽压力COLDREHEATERSTEAMPRESSURE | DAS | S | AI | 4~20mA | MPa | 0 | 5 |  | 0 | 9
48 |  | 10LBA40CP103 | J0202-01 | 汽缸加热夹层进汽箱蒸汽压力STEAMCOLLECTORFORCASINGSANDWITHHEATINGSTEAMPRESS. | DAS | S | AI | 4~20mA | MPa | 0 | 6 |  | 0 | 10
12 |  | 10LBA11CP102 | J0202-01 | 高压缸左侧进汽管压力HPCYLINDERLEFTSIDEINLETPIPESTEAMPRESS. | MCS | S | AI | 4~20mA | MPa | 0 | 20 |  | 0 | 11
5 |  | 10LBA10CP110 | J0202-01 | 高压缸进汽母管压力HPCYLINDERINLETHEADERSTEAMPRESS. | MCS | S | AI | 4~20mA | MPa | 0 | 20 |  | 0 | 12
1089 |  | 10LBW40CP103 | J0202-07 | 低压轴封母管压力LPGLANDSEALSTEAMPRESS. | DAS | S | AI | 4~20mA | MPa | -0.1 | 0.4 |  | 0 | 13
1032 |  | 10LBG11CP101 | J0202-06 | 1号机组低再至辅汽联箱蒸汽压力UNIT1COLDREHEATSTEAMTOAUXILIARYSTEAMHEADERSTEAMPRESSURE | DAS | S | AI | 4~20mA | MPa | 0 | 4 |  | 0 | 14
1031 |  | 10LBG11CF101 | J0202-06 | 1号机组低再至辅汽联箱蒸汽流量UNIT1COLDREHEATSTEAMTOAUXILIARYSTEAMHEADERSTEAMFLOW | DAS | S | AI | 4~20mA | t/h | 0 | 50 |  | 0 | 15
469 | 2 | 10LBQ20CP101 | J0202-03 | 2段抽汽压力NO.2EXTRACTIONSTEAMPRESSURE | DAS | S | AI | 4~20mA | MPa | 0 | 6 |  | 1 | 1
515 | 2 | 10LBR20AA001XQ01 | J0202-03 | 小机B排汽阀阀位反馈BFPTBEXHAUSTSTEAMVALVEPOSITION | SCS | S | AI | 4~20mA |  |  |  |  | 1 | 2
544 | 2 | 10LBR40CF102 | J0202-03 | 4段抽汽至小机流量2NO.4EXTRACTIONSTEAMTOBFPTURBINESFLOW2 | DAS | S | AI | 4~20mA | t/h | 0 | 44.291 |  | 1 | 3
613 | 2 | 10LBS40CP103 | J0202-03 | 4段抽汽至除氧器压力2NO.4EXTRACTIONSTEAMTODEAERATORSTEAMPRESSURE2 | DAS | S | AI | 4~20mA | MPa | 0 | 1.2 |  | 1 | 4
688 |  | 10LBS80CP101 | J0202-03 | 8段抽汽压力NO.8EXTRACTIONSTEAMPRESSURE | DAS | S | AI | 4~20mA | MPa | 0 | 0.15 |  | 1 | 5
686 |  | 10LBS70CP101 | J0202-03 | 7段抽汽压力NO.7EXTRACTIONSTEAMPRESSURE | DAS | S | AI | 4~20mA | MPa | 0 | 0.3 |  | 1 | 6
495 | 3 | 10LBQ30CP101 | J0202-03 | 3段抽汽压力NO.3EXTRACTIONSTEAMPRESSURE | DAS | S | AI | 4~20mA | MPa | 0 | 4 |  | 2 | 1
414 | 1 | 10LBG60CT201 | J0202-03 | 辅汽至小机A供汽母管疏水管壁温度AUXILIARYSTEAMTOBFPTURBINEAHEADERPIPEDRAINPIPEMETALTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 0 | 1
440 | 1 | 10LBQ10CT202 | J0202-03 | 1段抽汽关断阀后疏水管壁温度1NO.1EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINPIPEMETALTEMPERATURE1 | DAS | S | AI | TC_K | ℃ |  |  |  | 0 | 2
443 | 1 | 10LBQ10CT602 | J0202-03 | 1段抽汽逆止阀前上部汽温NO.1EXTRACTIONSTEAMCHECKVALVEFRONTPIPETOPSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 0 | 3
445 | 1 | 10LBQ10CT604 | J0202-03 | 1段抽汽关断阀后上部汽温NO.1EXTRACTIONSTEAMCUTOFFVALVEBACKPIPETOPSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 0 | 4
473 | 1 | 10LBQ20CT602 | J0202-03 | 2段抽汽逆止阀前上部汽温NO.2EXTRACTIONSTEAMCHECKVALVEFRONTPIPETOPSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 0 | 5
475 | 1 | 10LBQ20CT604 | J0202-03 | 2段抽汽关断阀后上部汽温NO.2EXTRACTIONSTEAMCUTOFFVALVEBACKPIPETOPSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 0 | 6
499 | 1 | 10LBQ30CT602 | J0202-03 | 3段抽汽逆止阀前上部汽温NO.3EXTRACTIONSTEAMCHECKVALVEFRONTPIPETOPSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 0 | 7
501 | 1 | 10LBQ30CT604 | J0202-03 | 3段抽汽关断阀后上部汽温NO.3EXTRACTIONSTEAMCUTOFFVALVEBACKPIPETOPSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 0 | 8
546 | 1 | 10LBR40CT202 | J0202-03 | 小机A进汽母管疏水管壁温度BFPTAINLETSTEAMHEADERPIPEDRAINPIPEMETALTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 0 | 9
548 | 1 | 10LBR40CT601 | J0202-03 | 小机A进汽母管上部汽温BFPTAINLETHEADERPIPETOPSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 0 | 10
550 | 1 | 10LBR40CT603 | J0202-03 | 小机B进汽母管上部汽温BFPTBINLETHEADERPIPETOPSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 0 | 11
615 | 1 | 10LBS40CT202 | J0202-03 | 4段抽汽关断阀后疏水管壁温度2NO.4EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINPIPEMETALTEMPERATURE2 | DAS | S | AI | TC_K | ℃ |  |  |  | 0 | 12
619 | 1 | 10LBS40CT602 | J0202-03 | 4段抽汽逆止阀前上部汽温NO.4EXTRACTIONSTEAMCHECKVALVEFRONTPIPETOPSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 0 | 13
621 | 1 | 10LBS40CT604 | J0202-03 | 4段抽汽关断阀后上部汽温NO.4EXTRACTIONSTEAMCUTOFFVALVEBACKPIPETOPSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 0 | 14
651 | 1 | 10LBS50CT602 | J0202-03 | 5段抽汽逆止阀前上部汽温NO.5EXTRACTIONSTEAMCHECKVALVEFRONTPIPETOPSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 0 | 15
653 | 1 | 10LBS50CT604 | J0202-03 | 5段抽汽关断阀后上部汽温NO.5EXTRACTIONSTEAMCUTOFFVALVEBACKPIPETOPSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 1 | 1
682 | 1 | 10LBS60CT602 | J0202-03 | 6段抽汽逆止阀前上部汽温NO.6EXTRACTIONSTEAMCHECKVALVEFRONTPIPETOPSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 1 | 2
684 | 1 | 10LBS60CT604 | J0202-03 | 6段抽汽关断阀后上部汽温NO.6EXTRACTIONSTEAMCUTOFFVALVEBACKPIPETOPSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 1 | 3
1023 | 1 | 10LBG10CT601 | J0202-06 | 1号机组辅汽联箱温度1UNIT1AUXILIARYSTEAMHEADERTEMPERATURE1 | DAS | S | AI | TC_K | ℃ | 0 | 350 |  | 1 | 4
1200 | 1 | 10LCH11CT201 | J0202-08 | 1号高加危急疏水管壁温度HP1EMERGENCYDRAINWATERPIPEMETALTEMPERATURE | DAS | S | AI | TC_K | ℃ | 0 | 300 |  | 1 | 5
471 |  | 10LBQ20CT202 | J0202-03 | 2段抽汽关断阀后疏水管壁温度NO.2EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINPIPEMETALTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 1 | 6
470 |  | 10LBQ20CT201 | J0202-03 | 2段抽汽逆止阀前疏水管壁温度NO.2EXTRACTIONSTEAMCHECKVALVEFRONTDRAINPIPEMETALTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 1 | 7
442 |  | 10LBQ10CT601 | J0202-03 | 1段抽汽温度NO.1EXTRACTIONSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 1 | 8
439 |  | 10LBQ10CT201 | J0202-03 | 1段抽汽逆止阀前疏水管壁温度NO.1EXTRACTIONSTEAMCHECKVALVEFRONTDRAINPIPEMETALTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 1 | 9
545 |  | 10LBR40CT201 | J0202-03 | 4段抽汽至小机供汽母管疏水管壁温度NO.4EXTRACTIONSTEAMTOBFPTURBINESHEADERPIPEDRAINPIPEMETALTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 1 | 10
498 |  | 10LBQ30CT601 | J0202-03 | 3段抽汽温度NO.3EXTRACTIONSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 1 | 11
497 |  | 10LBQ30CT202 | J0202-03 | 3段抽汽关断阀后疏水管壁温度NO.3EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINPIPEMETALTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 1 | 12
496 |  | 10LBQ30CT201 | J0202-03 | 3段抽汽逆止阀前疏水管壁温度NO.3EXTRACTIONSTEAMCHECKVALVEFRONTDRAINPIPEMETALTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 1 | 13
472 |  | 10LBQ20CT601 | J0202-03 | 2段抽汽温度NO.2EXTRACTIONSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 1 | 14
650 |  | 10LBS50CT601 | J0202-03 | 5段抽汽温度NO.5EXTRACTIONSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 1 | 15
415 | 2 | 10LBG60CT202 | J0202-03 | 辅汽至小机B供汽母管疏水管壁温度AUXILIARYSTEAMTOBFPTURBINEBHEADERPIPEDRAINPIPEMETALTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 2 | 1
441 | 2 | 10LBQ10CT203 | J0202-03 | 1段抽汽关断阀后疏水管壁温度2NO.1EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINPIPEMETALTEMPERATURE2 | DAS | S | AI | TC_K | ℃ |  |  |  | 2 | 2
444 | 2 | 10LBQ10CT603 | J0202-03 | 1段抽汽逆止阀前下部汽温NO.1EXTRACTIONSTEAMCHECKVALVEFRONTPIPEBOTTOMSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 2 | 3
446 | 2 | 10LBQ10CT605 | J0202-03 | 1段抽汽关断阀后下部汽温NO.1EXTRACTIONSTEAMCUTOFFVALVEBACKPIPEBOTTOMSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 2 | 4
474 | 2 | 10LBQ20CT603 | J0202-03 | 2段抽汽逆止阀前下部汽温NO.2EXTRACTIONSTEAMCHECKVALVEFRONTPIPEBOTTOMSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 2 | 5
476 | 2 | 10LBQ20CT605 | J0202-03 | 2段抽汽关断阀后下部汽温NO.2EXTRACTIONSTEAMCUTOFFVALVEBACKPIPEBOTTOMSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 2 | 6
500 | 2 | 10LBQ30CT603 | J0202-03 | 3段抽汽逆止阀前下部汽温NO.3EXTRACTIONSTEAMCHECKVALVEFRONTPIPEBOTTOMSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 2 | 7
502 | 2 | 10LBQ30CT605 | J0202-03 | 3段抽汽关断阀后下部汽温NO.3EXTRACTIONSTEAMCUTOFFVALVEBACKPIPEBOTTOMSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 2 | 8
547 | 2 | 10LBR40CT203 | J0202-03 | 小机B进汽母管疏水管壁温度BFPTBINLETSTEAMHEADERPIPEDRAINPIPEMETALTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 2 | 9
549 | 2 | 10LBR40CT602 | J0202-03 | 小机A进汽母管下部汽温BFPTAINLETHEADERPIPEBOTTOMSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 2 | 10
551 | 2 | 10LBR40CT604 | J0202-03 | 小机B进汽母管下部汽温BFPTBINLETHEADERPIPEBOTTOMSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 2 | 11
616 | 2 | 10LBS40CT203 | J0202-03 | 4段抽汽关断阀后疏水管壁温度3NO.4EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINPIPEMETALTEMPERATURE3 | DAS | S | AI | TC_K | ℃ |  |  |  | 2 | 12
620 | 2 | 10LBS40CT603 | J0202-03 | 4段抽汽逆止阀前下部汽温NO.4EXTRACTIONSTEAMCHECKVALVEFRONTPIPEBOTTOMSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 2 | 13
622 | 2 | 10LBS40CT605 | J0202-03 | 4段抽汽关断阀后下部汽温NO.4EXTRACTIONSTEAMCUTOFFVALVEBACKPIPEBOTTOMSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 2 | 14
652 | 2 | 10LBS50CT603 | J0202-03 | 5段抽汽逆止阀前下部汽温NO.5EXTRACTIONSTEAMCHECKVALVEFRONTPIPEBOTTOMSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 2 | 15
654 | 2 | 10LBS50CT605 | J0202-03 | 5段抽汽关断阀后下部汽温NO.5EXTRACTIONSTEAMCUTOFFVALVEBACKPIPEBOTTOMSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 3 | 1
683 | 2 | 10LBS60CT603 | J0202-03 | 6段抽汽逆止阀前下部汽温NO.6EXTRACTIONSTEAMCHECKVALVEFRONTPIPEBOTTOMSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 3 | 2
685 | 2 | 10LBS60CT605 | J0202-03 | 6段抽汽关断阀后下部汽温NO.6EXTRACTIONSTEAMCUTOFFVALVEBACKPIPEBOTTOMSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 3 | 3
1024 | 2 | 10LBG10CT602 | J0202-06 | 1号机组辅汽联箱温度2UNIT1AUXILIARYSTEAMHEADERTEMPERATURE2 | DAS | S | AI | TC_K | ℃ | 0 | 350 |  | 3 | 4
1208 | 2 | 10LCH21CT201 | J0202-08 | 2号高加危急疏水管壁温度HP2EMERGENCYDRAINWATERPIPEMETALTEMPERATURE | DAS | S | AI | TC_K | ℃ | 0 | 250 |  | 3 | 5
649 |  | 10LBS50CT203 | J0202-03 | 5段抽汽逆止阀前疏水管壁温度1NO.5EXTRACTIONSTEAMCHECKVALVEFRONTDRAINPIPEMETALTEMPERATURE1 | DAS | S | AI | TC_K | ℃ |  |  |  | 3 | 6
648 |  | 10LBS50CT202 | J0202-03 | 5段抽汽关断阀后疏水管壁温度NO.5EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINPIPEMETALTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 3 | 7
647 |  | 10LBS50CT201 | J0202-03 | 5段抽汽逆止阀前疏水管壁温度2NO.5EXTRACTIONSTEAMCHECKVALVEFRONTDRAINPIPEMETALTEMPERATURE2 | DAS | S | AI | TC_K | ℃ |  |  |  | 3 | 8
623 |  | 10LBS40CT606 | J0202-03 | 4段抽汽至除氧器温度NO.4EXTRACTIONSTEAMTODEAERATORSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 3 | 9
618 |  | 10LBS40CT601 | J0202-03 | 4段抽汽温度NO.4EXTRACTIONSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 3 | 10
614 |  | 10LBS40CT201 | J0202-03 | 4段抽汽逆止阀1前疏水管壁温度NO.4EXTRACTIONSTEAMCHECKVALVE1FRONTDRAINPIPEMETALTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 3 | 11
1033 |  | 10LBG11CT601 | J0202-06 | 1号机组低再至辅汽联箱蒸汽温度UNIT1COLDREHEATSTEAMTOAUXILIARYSTEAMHEADERSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ | 0 | 350 |  | 3 | 12
690 |  | 10LBS40CT204 | J0202-04 | 4段抽汽逆止阀2前疏水管壁温度NO.4EXTRACTIONSTEAMCHECKVALVE2FRONTDRAINPIPEMETALTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 3 | 13
689 |  | 10LBS80CT601 | J0202-03 | 8段抽汽温度NO.8EXTRACTIONSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 3 | 14
687 |  | 10LBS70CT601 | J0202-03 | 7段抽汽温度NO.7EXTRACTIONSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 3 | 15
617 | 3 | 10LBS40CT205 | J0202-03 | 4段抽汽关断阀后疏水管壁温度1NO.4EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINPIPEMETALTEMPERATURE1 | DAS | S | AI | TC_K | ℃ |  |  |  | 4 | 1
1218 | 3 | 10LCH31CT201 | J0202-08 | 3号高加危急疏水管壁温度HP3EMERGENCYDRAINWATERPIPEMETALTEMPERATURE | DAS | S | AI | TC_K | ℃ | 0 | 200 |  | 4 | 2
681 |  | 10LBS60CT601 | J0202-03 | 6段抽汽温度NO.6EXTRACTIONSTEAMTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 4 | 3
680 |  | 10LBS60CT203 | J0202-03 | 6段抽汽逆止阀前疏水管壁温度1NO.6EXTRACTIONSTEAMCHECKVALVEFRONTDRAINPIPEMETALTEMPERATURE1 | DAS | S | AI | TC_K | ℃ |  |  |  | 4 | 4
679 |  | 10LBS60CT202 | J0202-03 | 6段抽汽关断阀后疏水管壁温度NO.6EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINPIPEMETALTEMPERATURE | DAS | S | AI | TC_K | ℃ |  |  |  | 4 | 5
678 |  | 10LBS60CT201 | J0202-03 | 6段抽汽逆止阀前疏水管壁温度2NO.6EXTRACTIONSTEAMCHECKVALVEFRONTDRAINPIPEMETALTEMPERATURE2 | DAS | S | AI | TC_K | ℃ |  |  |  | 4 | 6
1 | 1 | 10LBA10AA401XB01 | J0202-01 | 高压缸进汽疏水阀已开HPCYLINDERINLETSTEAMDRAINVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 0 | 1
2 | 1+ | 10LBA10AA401XB02 | J0202-01 | 高压缸进汽疏水阀已关HPCYLINDERINLETSTEAMDRAINVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 0 | 2
3 | 1+ | 10LBA10AA401XB03 | J0202-01 | 高压缸进汽疏水阀故障HPCYLINDERINLETSTEAMDRAINVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 0 | 3
8 | 1 | 10LBA11AA401XB01 | J0202-01 | 高压缸左侧进汽疏水阀已开HPCYLINDERLEFTSIDEINLETSTEAMDRAINVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 0 | 4
9 | 1+ | 10LBA11AA401XB02 | J0202-01 | 高压缸左侧进汽疏水阀已关HPCYLINDERLEFTSIDEINLETSTEAMDRAINVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 0 | 5
10 | 1+ | 10LBA11AA401XB03 | J0202-01 | 高压缸左侧进汽疏水阀故障HPCYLINDERLEFTSIDEINLETSTEAMDRAINVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 0 | 6
22 | 1 | 10LBA40AA001XB01 | J0202-01 | 汽缸加热夹层进汽箱进口电动门已开STEAMCOLLECTORFORCASINGSANDWITHHEATINGINLETMV.OPENED | SCS | S | DI | NO |  |  |  |  | 0 | 7
23 | 1+ | 10LBA40AA001XB02 | J0202-01 | 汽缸加热夹层进汽箱进口电动门已关STEAMCOLLECTORFORCASINGSANDWITHHEATINGINLETMV.CLOSED | SCS | S | DI | NO |  |  |  |  | 0 | 8
24 | 1+ | 10LBA40AA001XB03 | J0202-01 | 汽缸加热夹层进汽箱进口电动门故障STEAMCOLLECTORFORCASINGSANDWITHHEATINGINLETMV.FAULT | SCS | S | DI | NO |  |  |  |  | 0 | 9
25 | 1+ | 10LBA40AA001XB04 | J0202-01 | 汽缸加热夹层进汽箱进口电动门远控STEAMCOLLECTORFORCASINGSANDWITHHEATINGINLETMV.REMOTESERVICE | SCS | S | DI | NO |  |  |  |  | 0 | 10
28 | 1 | 10LBA40AA010XB01 | J0202-01 | 高压内外缸夹层进汽电动门1已开DOUBLELAYEROFHPCASINGINLETMV1OPENED | SCS | S | DI | NO |  |  |  |  | 0 | 11
29 | 1+ | 10LBA40AA010XB02 | J0202-01 | 高压内外缸夹层进汽电动门1已关DOUBLELAYEROFHPCASINGINLETMV1CLOSED | SCS | S | DI | NO |  |  |  |  | 0 | 12
30 | 1+ | 10LBA40AA010XB03 | J0202-01 | 高压内外缸夹层进汽电动门1故障DOUBLELAYEROFHPCASINGINLETMV1FAULT | SCS | S | DI | NO |  |  |  |  | 0 | 13
31 | 1+ | 10LBA40AA010XB04 | J0202-01 | 高压内外缸夹层进汽电动门1远控DOUBLELAYEROFHPCASINGINLETMV1REMOTESERVICE | SCS | S | DI | NO |  |  |  |  | 0 | 14
40 | 1 | 10LBA40AA402XB01 | J0202-01 | 汽缸加热夹层进汽箱疏水电动门已开STEAMCOLLECTORFORCASINGSANDWITHHEATINGDRAINWATERMV.OPENED | SCS | S | DI | NO |  |  |  |  | 1 | 1 | 手工处理,因为设备相关信息
41 | 1+ | 10LBA40AA402XB02 | J0202-01 | 汽缸加热夹层进汽箱疏水电动门已关STEAMCOLLECTORFORCASINGSANDWITHHEATINGDRAINWATERMV.CLOSED | SCS | S | DI | NO |  |  |  |  | 1 | 2
42 | 1+ | 10LBA40AA402XB03 | J0202-01 | 汽缸加热夹层进汽箱疏水电动门故障STEAMCOLLECTORFORCASINGSANDWITHHEATINGDRAINWATERMV.FAULT | SCS | S | DI | NO |  |  |  |  | 1 | 3
43 | 1+ | 10LBA40AA402XB04 | J0202-01 | 汽缸加热夹层进汽箱疏水电动门远控STEAMCOLLECTORFORCASINGSANDWITHHEATINGDRAINWATERMV.REMOTESERVICE | SCS | S | DI | NO |  |  |  |  | 1 | 4
53 | 1 | 10LBB20AA401XB01 | J0202-01 | 热再热蒸汽疏水阀已开HOTREHEATSTEAMDRAINVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 1 | 5
54 | 1+ | 10LBB20AA401XB02 | J0202-01 | 热再热蒸汽疏水阀已关HOTREHEATSTEAMDRAINVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 1 | 6
55 | 1+ | 10LBB20AA401XB03 | J0202-01 | 热再热蒸汽疏水阀故障HOTREHEATSTEAMDRAINVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 1 | 7
58 | 1 | 10LBB31AA401XB01 | J0202-01 | 中压缸左侧进汽疏水阀已开IPCYLINDERLEFTSIDEINLETSTEAMDRAINVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 1 | 8
59 | 1+ | 10LBB31AA401XB02 | J0202-01 | 中压缸左侧进汽疏水阀已关IPCYLINDERLEFTSIDEINLETSTEAMDRAINVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 1 | 9
60 | 1+ | 10LBB31AA401XB03 | J0202-01 | 中压缸左侧进汽疏水阀故障IPCYLINDERLEFTSIDEINLETSTEAMDRAINVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 1 | 10
72 | 1 | 10LBB40AA401XB01 | J0202-01 | 低旁前疏水阀已开DRAINVALVEBEFORELPBYPASSOPENED | SCS | S | DI | NO |  |  |  |  | 1 | 11
73 | 1+ | 10LBB40AA401XB02 | J0202-01 | 低旁前疏水阀已关DRAINVALVEBEFORELPBYPASSCLOSED | SCS | S | DI | NO |  |  |  |  | 1 | 12
74 | 1+ | 10LBB40AA401XB03 | J0202-01 | 低旁前疏水阀故障DRAINVALVEBEFORELPBYPASSFAULT | SCS | S | DI | NO |  |  |  |  | 1 | 13
81 | 1 | 10LBC10AA401XB01 | J0202-01 | 右侧高排逆止阀前疏水阀已开DRAINVALVEBEFORERIGHTSIDEHPCYLINDEREXHAUSTEDSTEAMCHECKVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 1 | 14
82 | 1+ | 10LBC10AA401XB02 | J0202-01 | 右侧高排逆止阀前疏水阀已关DRAINVALVEBEFORERIGHTSIDEHPCYLINDEREXHAUSTEDSTEAMCHECKVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 1 | 15
83 | 1+ | 10LBC10AA401XB03 | J0202-01 | 右侧高排逆止阀前疏水阀故障DRAINVALVEBEFORERIGHTSIDEHPCYLINDEREXHAUSTEDSTEAMCHECKVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 1 | 16
85 | 1 | 10LBC10AA403XB01 | J0202-01 | 左侧高排逆止阀前疏水阀已开DRAINVALVEBEFORELEFTSIDEHPCYLINDEREXHAUSTEDSTEAMCHECKVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 2 | 1
86 | 1+ | 10LBC10AA403XB02 | J0202-01 | 左侧高排逆止阀前疏水阀已关DRAINVALVEBEFORELEFTSIDEHPCYLINDEREXHAUSTEDSTEAMCHECKVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 2 | 2
87 | 1+ | 10LBC10AA403XB03 | J0202-01 | 左侧高排逆止阀前疏水阀故障DRAINVALVEBEFORELEFTSIDEHPCYLINDEREXHAUSTEDSTEAMCHECKVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 2 | 3
89 | 1 | 10LBC10AA405XB01 | J0202-01 | 高排逆止阀后#2疏水罐疏水阀已开THEDRAINVALVEFORNo.2DRAINVESSELAFTERHPEXHAUSTEDSTEAMCHECKVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 2 | 4
90 | 1+ | 10LBC10AA405XB02 | J0202-01 | 高排逆止阀后#2疏水罐疏水阀已关THEDRAINVALVEFORNo.2DRAINVESSELAFTERHPEXHAUSTEDSTEAMCHECKVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 2 | 5
91 | 1+ | 10LBC10AA405XB03 | J0202-01 | 高排逆止阀后#2疏水罐疏水阀故障THEDRAINVALVEFORNo.2DRAINVESSELAFTERHPEXHAUSTEDSTEAMCHECKVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 2 | 6
93 | 1 | 10LBC10AA407XB01 | J0202-01 | 高排逆止阀后#1疏水罐疏水阀已开THEDRAINVALVEFORNo.1DRAINVESSELAFTERHPEXHAUSTEDSTEAMCHECKVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 2 | 7
94 | 1+ | 10LBC10AA407XB02 | J0202-01 | 高排逆止阀后#1疏水罐疏水阀已关THEDRAINVALVEFORNo.1DRAINVESSELAFTERHPEXHAUSTEDSTEAMCHECKVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 2 | 8
95 | 1+ | 10LBC10AA407XB03 | J0202-01 | 高排逆止阀后#1疏水罐疏水阀故障THEDRAINVALVEFORNo.1DRAINVESSELAFTERHPEXHAUSTEDSTEAMCHECKVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 2 | 9
97 | 1 | 10LBC10AA411XB01 | J0202-01 | 高排逆止阀后#3疏水罐疏水阀已开THEDRAINVALVEFORNo.3DRAINVESSELAFTERHPEXHAUSTEDSTEAMCHECKVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 2 | 10
98 | 1+ | 10LBC10AA411XB02 | J0202-01 | 高排逆止阀后#3疏水罐疏水阀已关THEDRAINVALVEFORNo.3DRAINVESSELAFTERHPEXHAUSTEDSTEAMCHECKVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 2 | 11
99 | 1+ | 10LBC10AA411XB03 | J0202-01 | 高排逆止阀后#3疏水罐疏水阀故障THEDRAINVALVEFORNo.3DRAINVESSELAFTERHPEXHAUSTEDSTEAMCHECKVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 2 | 12
101 | 1 | 10LBC10AA413XB01 | J0202-01 | 高排逆止阀后#4疏水罐疏水阀已开THEDRAINVALVEFORNo.4DRAINVESSELAFTERHPEXHAUSTEDSTEAMCHECKVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 2 | 13
102 | 1+ | 10LBC10AA413XB02 | J0202-01 | 高排逆止阀后#4疏水罐疏水阀已关THEDRAINVALVEFORNo.4DRAINVESSELAFTERHPEXHAUSTEDSTEAMCHECKVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 2 | 14
103 | 1+ | 10LBC10AA413XB03 | J0202-01 | 高排逆止阀后#4疏水罐疏水阀故障THEDRAINVALVEFORNo.4DRAINVESSELAFTERHPEXHAUSTEDSTEAMCHECKVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 2 | 15
105 | 1 | 10LBC10AA415XB01 | J0202-01 | 高排逆止阀后#5疏水罐疏水阀已开THEDRAINVALVEFORNo.5DRAINVESSELAFTERHPEXHAUSTEDSTEAMCHECKVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 3 | 1
106 | 1+ | 10LBC10AA415XB02 | J0202-01 | 高排逆止阀后#5疏水罐疏水阀已关THEDRAINVALVEFORNo.5DRAINVESSELAFTERHPEXHAUSTEDSTEAMCHECKVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 3 | 2
107 | 1+ | 10LBC10AA415XB03 | J0202-01 | 高排逆止阀后#5疏水罐疏水阀故障THEDRAINVALVEFORNo.5DRAINVESSELAFTERHPEXHAUSTEDSTEAMCHECKVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 3 | 3
109 | 1 | 10LBC10AA425XB01 | J0202-01 | VV阀前疏水阀已开DRAINVALVEBEFOREVVVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 3 | 4
110 | 1+ | 10LBC10AA425XB02 | J0202-01 | VV阀前疏水阀已关DRAINVALVEBEFOREVVVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 3 | 5
111 | 1+ | 10LBC10AA425XB03 | J0202-01 | VV阀前疏水阀故障DRAINVALVEBEFOREVVVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 3 | 6
136 | 1 | 10LBC11AA201XB01 | J0202-01 | 左侧高排逆止阀已开LEFTSIDEHPCYLINDEREXHAUSTEDSTEAMCHECKVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 3 | 7
137 | 1+ | 10LBC11AA201XB02 | J0202-01 | 左侧高排逆止阀已关LEFTSIDEHPCYLINDEREXHAUSTEDSTEAMCHECKVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 3 | 8
138 | 1+ | 10LBC11AA201XB03 | J0202-01 | 左侧高排逆止阀故障LEFTSIDEHPCYLINDEREXHAUSTEDSTEAMCHECKVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 3 | 9
142 | 1 | 10LBC12AA201XB01 | J0202-01 | 右侧高排逆止阀已开RIGHTSIDEHPCYLINDEREXHAUSTEDSTEAMCHECKVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 3 | 10
143 | 1+ | 10LBC12AA201XB02 | J0202-01 | 右侧高排逆止阀已关RIGHTSIDEHPCYLINDEREXHAUSTEDSTEAMCHECKVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 3 | 11
144 | 1+ | 10LBC12AA201XB03 | J0202-01 | 右侧高排逆止阀故障RIGHTSIDEHPCYLINDEREXHAUSTEDSTEAMCHECKVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 3 | 12
148 | 1 | 10LBG23AA001XB01 | J0202-01 | 汽轮机预暖管道电动节流阀已开MOTORTHROTTLEVALVEFORPRE-WARMINGTURBINEOPENED | SCS | S | DI | NO |  |  |  |  | 3 | 13
149 | 1+ | 10LBG23AA001XB02 | J0202-01 | 汽轮机预暖管道电动节流阀已关MOTORTHROTTLEVALVEFORPRE-WARMINGTURBINECLOSED | SCS | S | DI | NO |  |  |  |  | 3 | 14
150 | 1+ | 10LBG23AA001XB03 | J0202-01 | 汽轮机预暖管道电动节流阀故障MOTORTHROTTLEVALVEFORPRE-WARMINGTURBINEFAULT | SCS | S | DI | NO |  |  |  |  | 3 | 15
151 | 1+ | 10LBG23AA001XB04 | J0202-01 | 汽轮机预暖管道电动节流阀远控MOTORTHROTTLEVALVEFORPRE-WARMINGTURBINEREMOTESERVICE | SCS | S | DI | NO |  |  |  |  | 4 | 1
154 | 1+ | 10LBG23AA002XB01 | J0202-01 | 汽轮机预暖管道电动节流阀已开MOTORISOLATEDVALVEFORPRE-WARMINGTURBINEOPENED | SCS | S | DI | NO |  |  |  |  | 4 | 2 | 完全同名信号
155 | 1+ | 10LBG23AA002XB02 | J0202-01 | 汽轮机预暖管道电动节流阀已关MOTORISOLATEDVALVEFORPRE-WARMINGTURBINECLOSED | SCS | S | DI | NO |  |  |  |  | 4 | 3
156 | 1+ | 10LBG23AA002XB03 | J0202-01 | 汽轮机预暖管道电动节流阀故障MOTORISOLATEDVALVEFORPRE-WARMINGTURBINEFAULT | SCS | S | DI | NO |  |  |  |  | 4 | 4
157 | 1+ | 10LBG23AA002XB04 | J0202-01 | 汽轮机预暖管道电动节流阀远控MOTORISOLATEDVALVEFORPRE-WARMINGTURBINEREMOTESERVICE | SCS | S | DI | NO |  |  |  |  | 4 | 5
410 | 1 | 10LBG60AA401XB01 | J0202-03 | 辅汽至小机A供汽母管疏水阀已开AUXILIARYSTEAMTOBFPTURBINEAHEADERPIPEDRAINVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 4 | 6
411 | 1+ | 10LBG60AA401XB02 | J0202-03 | 辅汽至小机A供汽母管疏水阀已关AUXILIARYSTEAMTOBFPTURBINEAHEADERPIPEDRAINVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 4 | 7
412 | 1+ | 10LBG60AA401XB03 | J0202-03 | 辅汽至小机A供汽母管疏水阀故障AUXILIARYSTEAMTOBFPTURBINEAHEADERPIPEDRAINVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 4 | 8
416 | 1 | 10LBQ10AA001XB01 | J0202-03 | 1段抽汽关断阀已开NO.1EXTRACTIONSTEAMCUTOFFVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 4 | 9
417 | 1+ | 10LBQ10AA001XB02 | J0202-03 | 1段抽汽关断阀已关NO.1EXTRACTIONSTEAMCUTOFFVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 4 | 10
418 | 1+ | 10LBQ10AA001XB03 | J0202-03 | 1段抽汽关断阀故障NO.1EXTRACTIONSTEAMCUTOFFVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 4 | 11
419 | 1+ | 10LBQ10AA001XB04 | J0202-03 | 1段抽汽关断阀远控NO.1EXTRACTIONSTEAMCUTOFFVALVEREMOTESERVICE | SCS | S | DI | NO |  |  |  |  | 4 | 12
422 | 1 | 10LBQ10AA201XB01 | J0202-03 | 1段抽汽逆止阀已开NO.1EXTRACTIONSTEAMCHECKVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 4 | 13
423 | 1+ | 10LBQ10AA201XB02 | J0202-03 | 1段抽汽逆止阀已关NO.1EXTRACTIONSTEAMCHECKVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 4 | 14
424 | 1+ | 10LBQ10AA201XB03 | J0202-03 | 1段抽汽逆止阀故障NO.1EXTRACTIONSTEAMCHECKVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 4 | 15
426 | 1+ | 10LBQ10AA401XB01 | J0202-03 | 1段抽汽逆止阀前疏水阀已开NO.1EXTRACTIONSTEAMCHECKVALVEFRONTDRAINVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 5 | 1
427 | 1+ | 10LBQ10AA401XB02 | J0202-03 | 1段抽汽逆止阀前疏水阀已关NO.1EXTRACTIONSTEAMCHECKVALVEFRONTDRAINVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 5 | 2
428 | 1+ | 10LBQ10AA401XB03 | J0202-03 | 1段抽汽逆止阀前疏水阀故障NO.1EXTRACTIONSTEAMCHECKVALVEFRONTDRAINVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 5 | 3
430 | 1 | 10LBQ10AA411XB01 | J0202-03 | 1段抽汽关断阀后疏水阀1已开NO.1EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVE1OPENED | SCS | S | DI | NO |  |  |  |  | 5 | 4
431 | 1+ | 10LBQ10AA411XB02 | J0202-03 | 1段抽汽关断阀后疏水阀1已关NO.1EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVE1CLOSED | SCS | S | DI | NO |  |  |  |  | 5 | 5
432 | 1+ | 10LBQ10AA411XB03 | J0202-03 | 1段抽汽关断阀后疏水阀1故障NO.1EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVE1FAULT | SCS | S | DI | NO |  |  |  |  | 5 | 6
434 | 1 | 10LBQ10AA432XB01 | J0202-03 | 1段抽汽关断阀后疏水阀2已开NO.1EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVE2OPENED | SCS | S | DI | NO |  |  |  |  | 5 | 7
435 | 1+ | 10LBQ10AA432XB02 | J0202-03 | 1段抽汽关断阀后疏水阀2已关NO.1EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVE2CLOSED | SCS | S | DI | NO |  |  |  |  | 5 | 8
436 | 1+ | 10LBQ10AA432XB03 | J0202-03 | 1段抽汽关断阀后疏水阀2故障NO.1EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVE2FAULT | SCS | S | DI | NO |  |  |  |  | 5 | 9
447 | 1 | 10LBQ20AA001XB01 | J0202-03 | 2段抽汽关断阀已开NO.2EXTRACTIONSTEAMCUTOFFVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 5 | 10
448 | 1+ | 10LBQ20AA001XB02 | J0202-03 | 2段抽汽关断阀已关NO.2EXTRACTIONSTEAMCUTOFFVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 5 | 11
449 | 1+ | 10LBQ20AA001XB03 | J0202-03 | 2段抽汽关断阀故障NO.2EXTRACTIONSTEAMCUTOFFVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 5 | 12
450 | 1+ | 10LBQ20AA001XB04 | J0202-03 | 2段抽汽关断阀远控NO.2EXTRACTIONSTEAMCUTOFFVALVEREMOTESERVICE | SCS | S | DI | NO |  |  |  |  | 5 | 13
453 | 1 | 10LBQ20AA201XB01 | J0202-03 | 2段抽汽逆止阀已开NO.2EXTRACTIONSTEAMCHECKVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 5 | 14 | 手工处理,因为设备相关信息
454 | 1+ | 10LBQ20AA201XB02 | J0202-03 | 2段抽汽逆止阀已关NO.2EXTRACTIONSTEAMCHECKVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 5 | 15
455 | 1+ | 10LBQ20AA201XB03 | J0202-03 | 2段抽汽逆止阀故障NO.2EXTRACTIONSTEAMCHECKVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 6 | 1
457 | 1+ | 10LBQ20AA401XB01 | J0202-03 | 2段抽汽逆止阀前疏水阀已开NO.2EXTRACTIONSTEAMCHECKVALVEFRONTDRAINVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 6 | 2
458 | 1+ | 10LBQ20AA401XB02 | J0202-03 | 2段抽汽逆止阀前疏水阀已关NO.2EXTRACTIONSTEAMCHECKVALVEFRONTDRAINVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 6 | 3
459 | 1+ | 10LBQ20AA401XB03 | J0202-03 | 2段抽汽逆止阀前疏水阀故障NO.2EXTRACTIONSTEAMCHECKVALVEFRONTDRAINVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 6 | 4
461 | 1 | 10LBQ20AA411XB01 | J0202-03 | 2段抽汽关断阀后疏水阀已开NO.2EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 6 | 5
462 | 1+ | 10LBQ20AA411XB02 | J0202-03 | 2段抽汽关断阀后疏水阀已关NO.2EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 6 | 6
463 | 1+ | 10LBQ20AA411XB03 | J0202-03 | 2段抽汽关断阀后疏水阀故障NO.2EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 6 | 7
477 | 1 | 10LBQ30AA001XB01 | J0202-03 | 3段抽汽关断阀已开NO.3EXTRACTIONSTEAMCUTOFFVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 6 | 8
478 | 1+ | 10LBQ30AA001XB02 | J0202-03 | 3段抽汽关断阀已关NO.3EXTRACTIONSTEAMCUTOFFVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 6 | 9
479 | 1+ | 10LBQ30AA001XB03 | J0202-03 | 3段抽汽关断阀故障NO.3EXTRACTIONSTEAMCUTOFFVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 6 | 10
480 | 1+ | 10LBQ30AA001XB04 | J0202-03 | 3段抽汽关断阀远控NO.3EXTRACTIONSTEAMCUTOFFVALVEREMOTESERVICE | SCS | S | DI | NO |  |  |  |  | 6 | 11
483 | 1 | 10LBQ30AA201XB01 | J0202-03 | 3段抽汽逆止阀已开NO.3EXTRACTIONSTEAMCHECKVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 6 | 12
484 | 1+ | 10LBQ30AA201XB02 | J0202-03 | 3段抽汽逆止阀已关NO.3EXTRACTIONSTEAMCHECKVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 6 | 13
485 | 1+ | 10LBQ30AA201XB03 | J0202-03 | 3段抽汽逆止阀故障NO.3EXTRACTIONSTEAMCHECKVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 6 | 14
487 | 1+ | 10LBQ30AA401XB01 | J0202-03 | 3段抽汽逆止阀前疏水阀已开NO.3EXTRACTIONSTEAMCHECKVALVEFRONTDRAINVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 6 | 15
488 | 1+ | 10LBQ30AA401XB02 | J0202-03 | 3段抽汽逆止阀前疏水阀已关NO.3EXTRACTIONSTEAMCHECKVALVEFRONTDRAINVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 7 | 1
489 | 1+ | 10LBQ30AA401XB03 | J0202-03 | 3段抽汽逆止阀前疏水阀故障NO.3EXTRACTIONSTEAMCHECKVALVEFRONTDRAINVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 7 | 2
491 | 1 | 10LBQ30AA411XB01 | J0202-03 | 3段抽汽关断阀后疏水阀已开NO.3EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 7 | 3
492 | 1+ | 10LBQ30AA411XB02 | J0202-03 | 3段抽汽关断阀后疏水阀已关NO.3EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 7 | 4
493 | 1+ | 10LBQ30AA411XB03 | J0202-03 | 3段抽汽关断阀后疏水阀故障NO.3EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 7 | 5
503 | 1 | 10LBR10AA001XB01 | J0202-03 | 小机A排汽阀已开BFPTAEXHAUSTSTEAMVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 7 | 6
504 | 1+ | 10LBR10AA001XB02 | J0202-03 | 小机A排汽阀已关BFPTAEXHAUSTSTEAMVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 7 | 7
505 | 1+ | 10LBR10AA001XB03 | J0202-03 | 小机A排汽阀故障BFPTAEXHAUSTSTEAMVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 7 | 8
506 | 1+ | 10LBR10AA001XB04 | J0202-03 | 小机A排汽阀远控BFPTAEXHAUSTSTEAMVALVEREMOTESERVICE | SCS | S | DI | NO |  |  |  |  | 7 | 9
519 | 1 | 10LBR40AA011XB01 | J0202-03 | 4段抽汽至小机A供汽关断阀已开NO.4EXTRACTIONSTEAMTOBFPTACUTOFFVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 7 | 10
520 | 1+ | 10LBR40AA011XB02 | J0202-03 | 4段抽汽至小机A供汽关断阀已关NO.4EXTRACTIONSTEAMTOBFPTACUTOFFVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 7 | 11
521 | 1+ | 10LBR40AA011XB03 | J0202-03 | 4段抽汽至小机A供汽关断阀故障NO.4EXTRACTIONSTEAMTOBFPTACUTOFFVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 7 | 12
522 | 1+ | 10LBR40AA011XB04 | J0202-03 | 4段抽汽至小机A供汽关断阀远控NO.4EXTRACTIONSTEAMTOBFPTACUTOFFVALVEREMOTESERVICE | SCS | S | DI | NO |  |  |  |  | 7 | 13
531 | 1 | 10LBR40AA431XB01 | J0202-03 | 4段抽汽至小机供汽母管疏水阀已开NO.4EXTRACTIONSTEAMTOBFPTURBINESHEADERPIPEDRAINVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 7 | 14
532 | 1+ | 10LBR40AA431XB02 | J0202-03 | 4段抽汽至小机供汽母管疏水阀已关NO.4EXTRACTIONSTEAMTOBFPTURBINESHEADERPIPEDRAINVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 7 | 15
533 | 1+ | 10LBR40AA431XB03 | J0202-03 | 4段抽汽至小机供汽母管疏水阀故障NO.4EXTRACTIONSTEAMTOBFPTURBINESHEADERPIPEDRAINVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 8 | 1
535 | 1 | 10LBR40AA441XB01 | J0202-03 | 小机A进汽母管疏水阀已开BFPTAINLETSTEAMHEADERPIPEDRAINVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 8 | 2
536 | 1+ | 10LBR40AA441XB02 | J0202-03 | 小机A进汽母管疏水阀已关BFPTAINLETSTEAMHEADERPIPEDRAINVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 8 | 3
537 | 1+ | 10LBR40AA441XB03 | J0202-03 | 小机A进汽母管疏水阀故障BFPTAINLETSTEAMHEADERPIPEDRAINVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 8 | 4
552 | 1 | 10LBR60AA001XB01 | J0202-03 | 辅汽至小机A供汽关断阀已开AUXILIARYSTEAMTOBFPTACUTOFFVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 8 | 5
553 | 1+ | 10LBR60AA001XB02 | J0202-03 | 辅汽至小机A供汽关断阀已关AUXILIARYSTEAMTOBFPTACUTOFFVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 8 | 6
554 | 1+ | 10LBR60AA001XB03 | J0202-03 | 辅汽至小机A供汽关断阀故障AUXILIARYSTEAMTOBFPTACUTOFFVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 8 | 7
560 | 1 | 10LBR60AA403XB01 | J0202-03 | 辅汽至小机B供汽母管疏水阀已开AUXILIARYSTEAMTOBFPTURBINEBHEADERPIPEDRAINVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 8 | 8
561 | 1+ | 10LBR60AA403XB02 | J0202-03 | 辅汽至小机B供汽母管疏水阀已关AUXILIARYSTEAMTOBFPTURBINEBHEADERPIPEDRAINVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 8 | 9
562 | 1+ | 10LBR60AA403XB03 | J0202-03 | 辅汽至小机B供汽母管疏水阀故障AUXILIARYSTEAMTOBFPTURBINEBHEADERPIPEDRAINVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 8 | 10
564 | 1 | 10LBS40AA001XB01 | J0202-03 | 4段抽汽关断阀已开NO.4EXTRACTIONSTEAMCUTOFFVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 8 | 11
565 | 1+ | 10LBS40AA001XB02 | J0202-03 | 4段抽汽关断阀已关NO.4EXTRACTIONSTEAMCUTOFFVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 8 | 12
566 | 1+ | 10LBS40AA001XB03 | J0202-03 | 4段抽汽关断阀故障NO.4EXTRACTIONSTEAMCUTOFFVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 8 | 13
567 | 1+ | 10LBS40AA001XB04 | J0202-03 | 4段抽汽关断阀远控NO.4EXTRACTIONSTEAMCUTOFFVALVEREMOTESERVICE | SCS | S | DI | NO |  |  |  |  | 8 | 14
570 | 1 | 10LBS40AA002XB01 | J0202-03 | 4段抽汽至除氧器关断阀已开NO.4EXTRACTIONSTEAMTODEAERATORCUTOFFVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 8 | 15 | 手工处理,因为设备相关信息
571 | 1+ | 10LBS40AA002XB02 | J0202-03 | 4段抽汽至除氧器关断阀已关NO.4EXTRACTIONSTEAMTODEAERATORCUTOFFVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 9 | 1
572 | 1+ | 10LBS40AA002XB03 | J0202-03 | 4段抽汽至除氧器关断阀故障NO.4EXTRACTIONSTEAMTODEAERATORCUTOFFVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 9 | 2
573 | 1+ | 10LBS40AA002XB04 | J0202-03 | 4段抽汽至除氧器关断阀远控NO.4EXTRACTIONSTEAMTODEAERATORCUTOFFVALVEREMOTESERVICE | SCS | S | DI | NO |  |  |  |  | 9 | 3
576 | 1 | 10LBS40AA031XB01 | J0202-03 | 4段抽汽至辅汽关断阀已开NO.4EXTRACTIONSTEAMTOAUXILIARYSTEAMCUTOFFVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 9 | 4
577 | 1+ | 10LBS40AA031XB02 | J0202-03 | 4段抽汽至辅汽关断阀已关NO.4EXTRACTIONSTEAMTOAUXILIARYSTEAMCUTOFFVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 9 | 5
578 | 1+ | 10LBS40AA031XB03 | J0202-03 | 4段抽汽至辅汽关断阀故障NO.4EXTRACTIONSTEAMTOAUXILIARYSTEAMCUTOFFVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 9 | 6
579 | 1+ | 10LBS40AA031XB04 | J0202-03 | 4段抽汽至辅汽关断阀远控NO.4EXTRACTIONSTEAMTOAUXILIARYSTEAMCUTOFFVALVEREMOTESERVICE | SCS | S | DI | NO |  |  |  |  | 9 | 7
582 | 1 | 10LBS40AA201XB01 | J0202-03 | 4段抽汽逆止阀1已开NO.4EXTRACTIONSTEAMCHECKVALVE1OPENED | SCS | S | DI | NO |  |  |  |  | 9 | 8
583 | 1+ | 10LBS40AA201XB02 | J0202-03 | 4段抽汽逆止阀1已关NO.4EXTRACTIONSTEAMCHECKVALVE1CLOSED | SCS | S | DI | NO |  |  |  |  | 9 | 9
584 | 1+ | 10LBS40AA201XB03 | J0202-03 | 4段抽汽逆止阀1故障NO.4EXTRACTIONSTEAMCHECKVALVE1FAULT | SCS | S | DI | NO |  |  |  |  | 9 | 10
590 | 1 | 10LBS40AA401XB01 | J0202-03 | 4段抽汽逆止阀1前疏水阀已开NO.4EXTRACTIONSTEAMCHECKVALVE1FRONTDRAINVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 9 | 11
591 | 1+ | 10LBS40AA401XB02 | J0202-03 | 4段抽汽逆止阀1前疏水阀已关NO.4EXTRACTIONSTEAMCHECKVALVE1FRONTDRAINVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 9 | 12
592 | 1+ | 10LBS40AA401XB03 | J0202-03 | 4段抽汽逆止阀1前疏水阀故障NO.4EXTRACTIONSTEAMCHECKVALVE1FRONTDRAINVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 9 | 13
594 | 1 | 10LBS40AA411XB01 | J0202-03 | 4段抽汽关断阀后疏水阀2已开NO.4EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVE2OPENED | SCS | S | DI | NO |  |  |  |  | 9 | 14
595 | 1+ | 10LBS40AA411XB02 | J0202-03 | 4段抽汽关断阀后疏水阀2已关NO.4EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVE2CLOSED | SCS | S | DI | NO |  |  |  |  | 9 | 15
596 | 1+ | 10LBS40AA411XB03 | J0202-03 | 4段抽汽关断阀后疏水阀2故障NO.4EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVE2FAULT | SCS | S | DI | NO |  |  |  |  | 9 | 16
598 | 1 | 10LBS40AA412XB01 | J0202-03 | 4段抽汽逆止阀2前疏水阀已开NO.4EXTRACTIONSTEAMCHECKVALVE2FRONTDRAINVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 10 | 2
599 | 1+ | 10LBS40AA412XB02 | J0202-03 | 4段抽汽逆止阀2前疏水阀已关NO.4EXTRACTIONSTEAMCHECKVALVE2FRONTDRAINVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 10 | 3
600 | 1+ | 10LBS40AA412XB03 | J0202-03 | 4段抽汽逆止阀2前疏水阀故障NO.4EXTRACTIONSTEAMCHECKVALVE2FRONTDRAINVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 10 | 4
602 | 1 | 10LBS40AA416XB01 | J0202-03 | 4段抽汽关断阀后疏水阀1已开NO.4EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVE1OPENED | SCS | S | DI | NO |  |  |  |  | 10 | 5
603 | 1+ | 10LBS40AA416XB02 | J0202-03 | 4段抽汽关断阀后疏水阀1已关NO.4EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVE1CLOSED | SCS | S | DI | NO |  |  |  |  | 10 | 6
604 | 1+ | 10LBS40AA416XB03 | J0202-03 | 4段抽汽关断阀后疏水阀1故障NO.4EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVE1FAULT | SCS | S | DI | NO |  |  |  |  | 10 | 7
606 | 1 | 10LBS40AA421XB01 | J0202-03 | 4段抽汽关断阀后疏水阀3已开NO.4EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVE3OPENED | SCS | S | DI | NO |  |  |  |  | 10 | 8
607 | 1+ | 10LBS40AA421XB02 | J0202-03 | 4段抽汽关断阀后疏水阀3已关NO.4EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVE3CLOSED | SCS | S | DI | NO |  |  |  |  | 10 | 9
608 | 1+ | 10LBS40AA421XB03 | J0202-03 | 4段抽汽关断阀后疏水阀3故障NO.4EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVE3FAULT | SCS | S | DI | NO |  |  |  |  | 10 | 10
624 | 1 | 10LBS50AA001XB01 | J0202-03 | 5段抽汽关断阀已开NO.5EXTRACTIONSTEAMCUTOFFVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 10 | 11
625 | 1+ | 10LBS50AA001XB02 | J0202-03 | 5段抽汽关断阀已关NO.5EXTRACTIONSTEAMCUTOFFVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 10 | 12
626 | 1+ | 10LBS50AA001XB03 | J0202-03 | 5段抽汽关断阀故障NO.5EXTRACTIONSTEAMCUTOFFVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 10 | 13
627 | 1+ | 10LBS50AA001XB04 | J0202-03 | 5段抽汽关断阀远控NO.5EXTRACTIONSTEAMCUTOFFVALVEREMOTESERVICE | SCS | S | DI | NO |  |  |  |  | 10 | 14
630 | 1 | 10LBS50AA201XB01 | J0202-03 | 5段抽汽逆止阀已开NO.5EXTRACTIONSTEAMCHECKVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 10 | 15
631 | 1+ | 10LBS50AA201XB02 | J0202-03 | 5段抽汽逆止阀已关NO.5EXTRACTIONSTEAMCHECKVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 11 | 1
632 | 1+ | 10LBS50AA201XB03 | J0202-03 | 5段抽汽逆止阀故障NO.5EXTRACTIONSTEAMCHECKVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 11 | 2
634 | 1+ | 10LBS50AA401XB01 | J0202-03 | 5段抽汽逆止阀前疏水阀2已开NO.5EXTRACTIONSTEAMCHECKVALVEFRONTDRAINVALVE2OPENED | SCS | S | DI | NO |  |  |  |  | 11 | 3
635 | 1+ | 10LBS50AA401XB02 | J0202-03 | 5段抽汽逆止阀前疏水阀2已关NO.5EXTRACTIONSTEAMCHECKVALVEFRONTDRAINVALVE2CLOSED | SCS | S | DI | NO |  |  |  |  | 11 | 4
636 | 1+ | 10LBS50AA401XB03 | J0202-03 | 5段抽汽逆止阀前疏水阀2故障NO.5EXTRACTIONSTEAMCHECKVALVEFRONTDRAINVALVE2FAULT | SCS | S | DI | NO |  |  |  |  | 11 | 5
638 | 1 | 10LBS50AA411XB01 | J0202-03 | 5段抽汽关断阀后疏水阀已开NO.5EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 11 | 6
639 | 1+ | 10LBS50AA411XB02 | J0202-03 | 5段抽汽关断阀后疏水阀已关NO.5EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 11 | 7
640 | 1+ | 10LBS50AA411XB03 | J0202-03 | 5段抽汽关断阀后疏水阀故障NO.5EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 11 | 8
642 | 1 | 10LBS50AA431XB01 | J0202-03 | 5段抽汽逆止阀前疏水阀1已开NO.5EXTRACTIONSTEAMCHECKVALVEFRONTDRAINVALVE1OPENED | SCS | S | DI | NO |  |  |  |  | 11 | 9
643 | 1+ | 10LBS50AA431XB02 | J0202-03 | 5段抽汽逆止阀前疏水阀1已关NO.5EXTRACTIONSTEAMCHECKVALVEFRONTDRAINVALVE1CLOSED | SCS | S | DI | NO |  |  |  |  | 11 | 10
644 | 1+ | 10LBS50AA431XB03 | J0202-03 | 5段抽汽逆止阀前疏水阀1故障NO.5EXTRACTIONSTEAMCHECKVALVEFRONTDRAINVALVE1FAULT | SCS | S | DI | NO |  |  |  |  | 11 | 11
655 | 1 | 10LBS60AA001XB01 | J0202-03 | 6段抽汽关断阀已开NO.6EXTRACTIONSTEAMCUTOFFVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 11 | 12
656 | 1+ | 10LBS60AA001XB02 | J0202-03 | 6段抽汽关断阀已关NO.6EXTRACTIONSTEAMCUTOFFVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 11 | 13
657 | 1+ | 10LBS60AA001XB03 | J0202-03 | 6段抽汽关断阀故障NO.6EXTRACTIONSTEAMCUTOFFVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 11 | 14
658 | 1+ | 10LBS60AA001XB04 | J0202-03 | 6段抽汽关断阀远控NO.6EXTRACTIONSTEAMCUTOFFVALVEREMOTESERVICE | SCS | S | DI | NO |  |  |  |  | 11 | 15
661 | 1 | 10LBS60AA201XB01 | J0202-03 | 6段抽汽逆止阀已开NO.6EXTRACTIONSTEAMCHECKVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 12 | 1
662 | 1+ | 10LBS60AA201XB02 | J0202-03 | 6段抽汽逆止阀已关NO.6EXTRACTIONSTEAMCHECKVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 12 | 2
663 | 1+ | 10LBS60AA201XB03 | J0202-03 | 6段抽汽逆止阀故障NO.6EXTRACTIONSTEAMCHECKVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 12 | 3
665 | 1+ | 10LBS60AA401XB01 | J0202-03 | 6段抽汽逆止阀前疏水阀2已开NO.6EXTRACTIONSTEAMCHECKVALVEFRONTDRAINVALVE2OPENED | SCS | S | DI | NO |  |  |  |  | 12 | 4
666 | 1+ | 10LBS60AA401XB02 | J0202-03 | 6段抽汽逆止阀前疏水阀2已关NO.6EXTRACTIONSTEAMCHECKVALVEFRONTDRAINVALVE2CLOSED | SCS | S | DI | NO |  |  |  |  | 12 | 5
667 | 1+ | 10LBS60AA401XB03 | J0202-03 | 6段抽汽逆止阀前疏水阀2故障NO.6EXTRACTIONSTEAMCHECKVALVEFRONTDRAINVALVE2FAULT | SCS | S | DI | NO |  |  |  |  | 12 | 6
669 | 1 | 10LBS60AA411XB01 | J0202-03 | 6段抽汽关断阀后疏水阀已开NO.6EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 12 | 7
670 | 1+ | 10LBS60AA411XB02 | J0202-03 | 6段抽汽关断阀后疏水阀已关NO.6EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 12 | 8
671 | 1+ | 10LBS60AA411XB03 | J0202-03 | 6段抽汽关断阀后疏水阀故障NO.6EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 12 | 9
673 | 1 | 10LBS60AA431XB01 | J0202-03 | 6段抽汽逆止阀前疏水阀1已开NO.6EXTRACTIONSTEAMCHECKVALVEFRONTDRAINVALVE1OPENED | SCS | S | DI | NO |  |  |  |  | 12 | 10
674 | 1+ | 10LBS60AA431XB02 | J0202-03 | 6段抽汽逆止阀前疏水阀1已关NO.6EXTRACTIONSTEAMCHECKVALVEFRONTDRAINVALVE1CLOSED | SCS | S | DI | NO |  |  |  |  | 12 | 11
675 | 1+ | 10LBS60AA431XB03 | J0202-03 | 6段抽汽逆止阀前疏水阀1故障NO.6EXTRACTIONSTEAMCHECKVALVEFRONTDRAINVALVE1FAULT | SCS | S | DI | NO |  |  |  |  | 12 | 12
1015 | 1 | 10LBG10AA001XB01 | J0202-06 | 已开/启动锅炉至1号机组辅汽关断阀STARTUPBOILERTOUNIT1AUXILIARYSTEAMHEADERCUTOFFVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 12 | 13
1016 | 1+ | 10LBG10AA001XB02 | J0202-06 | 已关/启动锅炉至1号机组辅汽关断阀STARTUPBOILERTOUNIT1AUXILIARYSTEAMHEADERCUTOFFVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 12 | 14
1017 | 1+ | 10LBG10AA001XB03 | J0202-06 | 故障/启动锅炉至1号机组辅汽关断阀STARTUPBOILERTOUNIT1AUXILIARYSTEAMHEADERCUTOFFVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 12 | 15
1018 | 1+ | 10LBG10AA001XB04 | J0202-06 | 远控/启动锅炉至1号机组辅汽关断阀STARTUPBOILERTOUNIT1AUXILIARYSTEAMHEADERCUTOFFVALVEREMOTESERVICE | SCS | S | DI | NO |  |  |  |  | 13 | 1
1025 | 1+ | 10LBG11AA001XB01 | J0202-06 | 已开/1号机组低再至辅汽联箱蒸汽关断阀UNIT1COLDREHEATSTEAMTOAUXILIARYSTEAMHEADERSTEAMCUTOFFVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 13 | 2
1026 | 1+ | 10LBG11AA001XB02 | J0202-06 | 已关/1号机组低再至辅汽联箱蒸汽关断阀UNIT1COLDREHEATSTEAMTOAUXILIARYSTEAMHEADERSTEAMCUTOFFVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 13 | 3
1027 | 1+ | 10LBG11AA001XB03 | J0202-06 | 故障/1号机组低再至辅汽联箱蒸汽关断阀UNIT1COLDREHEATSTEAMTOAUXILIARYSTEAMHEADERSTEAMCUTOFFVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 13 | 4
1034 | 1+ | 10LBG30AA001XB01 | J0202-06 | 已开/1号机组辅汽至除氧器关断阀UNIT1AUXILIARYSTEAMTODEAERATORCUTOFFVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 13 | 5
1035 | 1+ | 10LBG30AA001XB02 | J0202-06 | 已关/1号机组辅汽至除氧器关断阀UNIT1AUXILIARYSTEAMTODEAERATORCUTOFFVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 13 | 6
1036 | 1+ | 10LBG30AA001XB03 | J0202-06 | 故障/1号机组辅汽至除氧器关断阀UNIT1AUXILIARYSTEAMTODEAERATORCUTOFFVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 13 | 7
1037 | 1+ | 10LBG30AA001XB04 | J0202-06 | 远控/1号机组辅汽至除氧器关断阀UNIT1AUXILIARYSTEAMTODEAERATORCUTOFFVALVEREMOTESERVICE | SCS | S | DI | NO |  |  |  |  | 13 | 8
1042 | 1+ | 10LBG50AA001XB01 | J0202-06 | 已开/1号机组辅汽至轴封供汽关断阀UNIT1AUXILIARYSTEAMTOGLANDSEALINGSYSTEMCUTOFFVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 13 | 9
1043 | 1+ | 10LBG50AA001XB02 | J0202-06 | 已关/1号机组辅汽至轴封供汽关断阀UNIT1AUXILIARYSTEAMTOGLANDSEALINGSYSTEMCUTOFFVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 13 | 10
1044 | 1+ | 10LBG50AA001XB03 | J0202-06 | 故障/1号机组辅汽至轴封供汽关断阀UNIT1AUXILIARYSTEAMTOGLANDSEALINGSYSTEMCUTOFFVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 13 | 11
1045 | 1+ | 10LBG50AA001XB04 | J0202-06 | 远控/1号机组辅汽至轴封供汽关断阀UNIT1AUXILIARYSTEAMTOGLANDSEALINGSYSTEMCUTOFFVALVEREMOTESERVICE | SCS | S | DI | NO |  |  |  |  | 13 | 12
1058 | 1+ | 10LBW20AA002XB01 | J0202-07 | 轴封供汽调节阀前电动门已开MVINFRONTOFGLANDSEALSYSTEMSTEAMPCVOPENED | SCS | S | DI | NO |  |  |  |  | 13 | 13
1059 | 1+ | 10LBW20AA002XB02 | J0202-07 | 轴封供汽调节阀前电动门已关MVINFRONTOFGLANDSEALSYSTEMSTEAMPCVCLOSED | SCS | S | DI | NO |  |  |  |  | 13 | 14
1060 | 1+ | 10LBW20AA002XB03 | J0202-07 | 轴封供汽调节阀前电动门故障MVINFRONTOFGLANDSEALSYSTEMSTEAMPCVFAULT | SCS | S | DI | NO |  |  |  |  | 13 | 15
1061 | 1+ | 10LBW20AA002XB04 | J0202-07 | 轴封供汽调节阀前电动门远控MVINFRONTOFGLANDSEALSYSTEMSTEAMPCVREMOTESERVICE | SCS | S | DI | NO |  |  |  |  | 14 | 1
1064 | 1 | 10LBW20AA003XB01 | J0202-07 | 轴封供汽调节阀旁路电动门已开BYPASSMVFORGLANDSEALSYSTEMSTEAMPCVOPENED | SCS | S | DI | NO |  |  |  |  | 14 | 2
1065 | 1+ | 10LBW20AA003XB02 | J0202-07 | 轴封供汽调节阀旁路电动门已关BYPASSMVFORGLANDSEALSYSTEMSTEAMPCVCLOSED | SCS | S | DI | NO |  |  |  |  | 14 | 3
1066 | 1+ | 10LBW20AA003XB03 | J0202-07 | 轴封供汽调节阀旁路电动门故障BYPASSMVFORGLANDSEALSYSTEMSTEAMPCVFAULT | SCS | S | DI | NO |  |  |  |  | 14 | 4
1067 | 1+ | 10LBW20AA003XB04 | J0202-07 | 轴封供汽调节阀旁路电动门远控BYPASSMVFORGLANDSEALSYSTEMSTEAMPCVREMOTESERVICE | SCS | S | DI | NO |  |  |  |  | 14 | 5
1073 | 1 | 10LBW21AA001XB01 | J0202-07 | 冷再至轴封供汽电动门已开MVFORGLANDSEALSYSTEMSTEAMFROMCOLDREHEATEROPENED | SCS | S | DI | NO |  |  |  |  | 14 | 6
1074 | 1+ | 10LBW21AA001XB02 | J0202-07 | 冷再至轴封供汽电动门已关MVFORGLANDSEALSYSTEMSTEAMFROMCOLDREHEATERCLOSED | SCS | S | DI | NO |  |  |  |  | 14 | 7
1075 | 1+ | 10LBW21AA001XB03 | J0202-07 | 冷再至轴封供汽电动门故障MVFORGLANDSEALSYSTEMSTEAMFROMCOLDREHEATERFAULT | SCS | S | DI | NO |  |  |  |  | 14 | 8
1076 | 1+ | 10LBW21AA001XB04 | J0202-07 | 冷再至轴封供汽电动门远控MVFORGLANDSEALSYSTEMSTEAMFROMCOLDREHEATERREMOTESERVICE | SCS | S | DI | NO |  |  |  |  | 14 | 9
1079 | 1 | 10LBW30AA002XB01 | J0202-07 | 轴封供汽溢流旁路电动门已开BYPASSMVFORGLANDSEALSYSTEMOVERFLOWSTEAMOPENCOMMANDOPENED | SCS | S | DI | NO |  |  |  |  | 14 | 10
1080 | 1+ | 10LBW30AA002XB02 | J0202-07 | 轴封供汽溢流旁路电动门已关BYPASSMVFORGLANDSEALSYSTEMOVERFLOWSTEAMOPENCOMMANDCLOSED | SCS | S | DI | NO |  |  |  |  | 14 | 11
1081 | 1+ | 10LBW30AA002XB03 | J0202-07 | 轴封供汽溢流旁路电动门故障BYPASSMVFORGLANDSEALSYSTEMOVERFLOWSTEAMOPENCOMMANDFAULT | SCS | S | DI | NO |  |  |  |  | 14 | 12
1082 | 1+ | 10LBW30AA002XB04 | J0202-07 | 轴封供汽溢流旁路电动门远控BYPASSMVFORGLANDSEALSYSTEMOVERFLOWSTEAMOPENCOMMANDREMOTESERVICE | SCS | S | DI | NO |  |  |  |  | 14 | 13
1093 | 1 | 10MAL10AA411XB01 | J0202-07 | 高压主汽阀疏水阀已开DRAINVALVEFORTSVOPENED | SCS | S | DI | NO |  |  |  |  | 14 | 14 | 手工处理,因为设备相关信息
1094 | 1+ | 10MAL10AA411XB02 | J0202-07 | 高压主汽阀疏水阀已关DRAINVALVEFORTSVCLOSED | SCS | S | DI | NO |  |  |  |  | 14 | 15
1095 | 1+ | 10MAL10AA411XB03 | J0202-07 | 高压主汽阀疏水阀故障DRAINVALVEFORTSVFAULT | SCS | S | DI | NO |  |  |  |  | 14 | 16
1097 | 1 | 10MAL10AA421XB01 | J0202-07 | 高压主调阀疏水阀已开DRAINVALVEFORCVOPENED | SCS | S | DI | NO |  |  |  |  | 15 | 2
1098 | 1+ | 10MAL10AA421XB02 | J0202-07 | 高压主调阀疏水阀已关DRAINVALVEFORCVCLOSED | SCS | S | DI | NO |  |  |  |  | 15 | 3
1099 | 1+ | 10MAL10AA421XB03 | J0202-07 | 高压主调阀疏水阀故障DRAINVALVEFORCVFAULT | SCS | S | DI | NO |  |  |  |  | 15 | 4
1101 | 1 | 10MAL10AA431XB01 | J0202-07 | 高压主调阀1后导汽管疏水阀已开DRAINVALVEFORSTEAMPIPEAFTERCV1OPENED | SCS | S | DI | NO |  |  |  |  | 15 | 5
1102 | 1+ | 10MAL10AA431XB02 | J0202-07 | 高压主调阀1后导汽管疏水阀已关DRAINVALVEFORSTEAMPIPEAFTERCV1CLOSED | SCS | S | DI | NO |  |  |  |  | 15 | 6
1103 | 1+ | 10MAL10AA431XB03 | J0202-07 | 高压主调阀1后导汽管疏水阀故障DRAINVALVEFORSTEAMPIPEAFTERCV1FAULT | SCS | S | DI | NO |  |  |  |  | 15 | 7
1113 | 1 | 10MAL10AA434XB01 | J0202-07 | 高压主调阀4后导汽管疏水阀已开DRAINVALVEFORSTEAMPIPEAFTERCV4OPENED | SCS | S | DI | NO |  |  |  |  | 15 | 8
1114 | 1+ | 10MAL10AA434XB02 | J0202-07 | 高压主调阀4后导汽管疏水阀已关DRAINVALVEFORSTEAMPIPEAFTERCV4CLOSED | SCS | S | DI | NO |  |  |  |  | 15 | 9
1115 | 1+ | 10MAL10AA434XB03 | J0202-07 | 高压主调阀4后导汽管疏水阀故障DRAINVALVEFORSTEAMPIPEAFTERCV4FAULT | SCS | S | DI | NO |  |  |  |  | 15 | 10
1117 | 1 | 10MAL10AA441XB01 | J0202-07 | 过桥汽封疏水阀已开DRAINVALVEFORBRIDGEGLANDSEALINGOPENED | SCS | S | DI | NO |  |  |  |  | 15 | 11
1118 | 1+ | 10MAL10AA441XB02 | J0202-07 | 过桥汽封疏水阀已关DRAINVALVEFORBRIDGEGLANDSEALINGCLOSED | SCS | S | DI | NO |  |  |  |  | 15 | 12
1119 | 1+ | 10MAL10AA441XB03 | J0202-07 | 过桥汽封疏水阀故障DRAINVALVEFORBRIDGEGLANDSEALINGFAULT | SCS | S | DI | NO |  |  |  |  | 15 | 13
1121 | 1 | 10MAL10AA451XB01 | J0202-07 | 中压进汽阀与中压缸疏水阀已开DRAINVALVEFORRSVANDIPCYLINDEROPENED | SCS | S | DI | NO |  |  |  |  | 15 | 14
1122 | 1+ | 10MAL10AA451XB02 | J0202-07 | 中压进汽阀与中压缸疏水阀已关DRAINVALVEFORRSVANDIPCYLINDERCLOSED | SCS | S | DI | NO |  |  |  |  | 15 | 15
1123 | 1+ | 10MAL10AA451XB03 | J0202-07 | 中压进汽阀与中压缸疏水阀故障DRAINVALVEFORRSVANDIPCYLINDERFAULT | SCS | S | DI | NO |  |  |  |  | 16 | 1
1132 | 1 | 10MAW10AA402XB01 | J0202-07 | 汽封冷却器紧急疏水阀已开GLANDSTEAMCONDENSEREMERGENCYDRAINVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 16 | 2
1133 | 1+ | 10MAW10AA402XB02 | J0202-07 | 汽封冷却器紧急疏水阀已关GLANDSTEAMCONDENSEREMERGENCYDRAINVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 16 | 3
1134 | 1+ | 10MAW10AA402XB03 | J0202-07 | 汽封冷却器紧急疏水阀故障GLANDSTEAMCONDENSEREMERGENCYDRAINVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 16 | 4
116 |  | 10LBC10CL004 | J0202-01 | 高排逆止阀后疏水罐2液位高THEDRAINVESSEL2LEVELHIGHAFTERHPCYLINDEREXHAUSTEDSTEAMCHECKVALVE | SCS | S | DI | NO | mm |  |  |  | 16 | 5
115 |  | 10LBC10CL003 | J0202-01 | 高排逆止阀后疏水罐2液位高高THEDRAINVESSEL2LEVELHIGHHIGHAFTERHPCYLINDEREXHAUSTEDSTEAMCHECKVALVE | SCS | S | DI | NO | mm |  |  |  | 16 | 6
114 |  | 10LBC10CL002 | J0202-01 | 高排逆止阀后疏水罐1液位高THEDRAINVESSEL1LEVELHIGHAFTERHPCYLINDEREXHAUSTEDSTEAMCHECKVALVE | SCS | S | DI | NO | mm |  |  |  | 16 | 7
113 |  | 10LBC10CL001 | J0202-01 | 高排逆止阀后疏水罐1液位高高THEDRAINVESSEL1LEVELHIGHHIGHAFTERHPCYLINDEREXHAUSTEDSTEAMCHECKVALVE | SCS | S | DI | NO | mm |  |  |  | 16 | 8
147 |  | 10LBC12CL002 | J0202-01 | 高排逆止阀2前疏水罐液位高THEDRAINVESSELLEVELHIGHBEFOREHPCYLINDEREXHAUSTEDSTEAMCHECKVALVE2 | SCS | S | DI | NO | mm |  |  |  | 16 | 9
146 |  | 10LBC12CL001 | J0202-01 | 高排逆止阀2前疏水罐液位高高THEDRAINVESSELLEVELHIGHHIGHBEFOREHPCYLINDEREXHAUSTEDSTEAMCHECKVALVE2 | SCS | S | DI | NO | mm |  |  |  | 16 | 10
141 |  | 10LBC11CL002 | J0202-01 | 高排逆止阀1前疏水罐液位高THEDRAINVESSELLEVELHIGHBEFOREHPCYLINDEREXHAUSTEDSTEAMCHECKVALVE1 | SCS | S | DI | NO | mm |  |  |  | 16 | 11
140 |  | 10LBC11CL001 | J0202-01 | 高排逆止阀1前疏水罐液位高高THEDRAINVESSELLEVELHIGHHIGHBEFOREHPCYLINDEREXHAUSTEDSTEAMCHECKVALVE1 | SCS | S | DI | NO | mm |  |  |  | 16 | 12
122 |  | 10LBC10CL010 | J0202-01 | 高排逆止阀后疏水罐5液位高THEDRAINVESSEL5LEVELHIGHAFTERHPCYLINDEREXHAUSTEDSTEAMCHECKVALVE | SCS | S | DI | NO | mm |  |  |  | 16 | 13
121 |  | 10LBC10CL009 | J0202-01 | 高排逆止阀后疏水罐5液位高高THEDRAINVESSEL5LEVELHIGHHIGHAFTERHPCYLINDEREXHAUSTEDSTEAMCHECKVALVE | SCS | S | DI | NO | mm |  |  |  | 16 | 14
120 |  | 10LBC10CL008 | J0202-01 | 高排逆止阀后疏水罐4液位高THEDRAINVESSEL4LEVELHIGHAFTERHPCYLINDEREXHAUSTEDSTEAMCHECKVALVE | SCS | S | DI | NO | mm |  |  |  | 16 | 15
15 | 2 | 10LBA12AA401XB01 | J0202-01 | 高压缸右侧进汽疏水阀已开HPCYLINDERRIGHTSIDEINLETSTEAMDRAINVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 17 | 1
16 | 2+ | 10LBA12AA401XB02 | J0202-01 | 高压缸右侧进汽疏水阀已关HPCYLINDERRIGHTSIDEINLETSTEAMDRAINVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 17 | 2
17 | 2+ | 10LBA12AA401XB03 | J0202-01 | 高压缸右侧进汽疏水阀故障HPCYLINDERRIGHTSIDEINLETSTEAMDRAINVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 17 | 3
34 | 2 | 10LBA40AA011XB01 | J0202-01 | 高压内外缸夹层进汽电动门2已开DOUBLELAYEROFHPCASINGINLETMV2OPENED | SCS | S | DI | NO |  |  |  |  | 17 | 4
35 | 2+ | 10LBA40AA011XB02 | J0202-01 | 高压内外缸夹层进汽电动门2已关DOUBLELAYEROFHPCASINGINLETMV2CLOSED | SCS | S | DI | NO |  |  |  |  | 17 | 5
36 | 2+ | 10LBA40AA011XB03 | J0202-01 | 高压内外缸夹层进汽电动门2故障DOUBLELAYEROFHPCASINGINLETMV2FAULT | SCS | S | DI | NO |  |  |  |  | 17 | 6
37 | 2+ | 10LBA40AA011XB04 | J0202-01 | 高压内外缸夹层进汽电动门2远控DOUBLELAYEROFHPCASINGINLETMV2REMOTESERVICE | SCS | S | DI | NO |  |  |  |  | 17 | 7
65 | 2 | 10LBB32AA401XB01 | J0202-01 | 中压缸右侧进汽疏水阀已开IPCYLINDERRIGHTSIDEINLETSTEAMDRAINVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 17 | 8
66 | 2+ | 10LBB32AA401XB02 | J0202-01 | 中压缸右侧进汽疏水阀已关IPCYLINDERRIGHTSIDEINLETSTEAMDRAINVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 17 | 9
67 | 2+ | 10LBB32AA401XB03 | J0202-01 | 中压缸右侧进汽疏水阀故障IPCYLINDERRIGHTSIDEINLETSTEAMDRAINVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 17 | 10
511 | 2 | 10LBR20AA001XB01 | J0202-03 | 小机B排汽阀已开BFPTBEXHAUSTSTEAMVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 17 | 11
512 | 2+ | 10LBR20AA001XB02 | J0202-03 | 小机B排汽阀已关BFPTBEXHAUSTSTEAMVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 17 | 12
513 | 2+ | 10LBR20AA001XB03 | J0202-03 | 小机B排汽阀故障BFPTBEXHAUSTSTEAMVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 17 | 13
514 | 2+ | 10LBR20AA001XB04 | J0202-03 | 小机B排汽阀远控BFPTBEXHAUSTSTEAMVALVEREMOTESERVICE | SCS | S | DI | NO |  |  |  |  | 17 | 14
525 | 2 | 10LBR40AA021XB01 | J0202-03 | 4段抽汽至小机B供汽关断阀已开NO.4EXTRACTIONSTEAMTOBFPTBCUTOFFVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 17 | 15
526 | 2+ | 10LBR40AA021XB02 | J0202-03 | 4段抽汽至小机B供汽关断阀已关NO.4EXTRACTIONSTEAMTOBFPTBCUTOFFVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 18 | 1
527 | 2+ | 10LBR40AA021XB03 | J0202-03 | 4段抽汽至小机B供汽关断阀故障NO.4EXTRACTIONSTEAMTOBFPTBCUTOFFVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 18 | 2
528 | 2+ | 10LBR40AA021XB04 | J0202-03 | 4段抽汽至小机B供汽关断阀远控NO.4EXTRACTIONSTEAMTOBFPTBCUTOFFVALVEREMOTESERVICE | SCS | S | DI | NO |  |  |  |  | 18 | 3
539 | 2 | 10LBR40AA451XB01 | J0202-03 | 小机B进汽母管疏水阀已开BFPTBINLETSTEAMHEADERPIPEDRAINVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 18 | 4
540 | 2+ | 10LBR40AA451XB02 | J0202-03 | 小机B进汽母管疏水阀已关BFPTBINLETSTEAMHEADERPIPEDRAINVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 18 | 5
541 | 2+ | 10LBR40AA451XB03 | J0202-03 | 小机B进汽母管疏水阀故障BFPTBINLETSTEAMHEADERPIPEDRAINVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 18 | 6
556 | 2 | 10LBR60AA002XB01 | J0202-03 | 辅汽至小机B供汽关断阀已开AUXILIARYSTEAMTOBFPTBCUTOFFVALVEOPENED | SCS | S | DI | NO |  |  |  |  | 18 | 7
557 | 2+ | 10LBR60AA002XB02 | J0202-03 | 辅汽至小机B供汽关断阀已关AUXILIARYSTEAMTOBFPTBCUTOFFVALVECLOSED | SCS | S | DI | NO |  |  |  |  | 18 | 8
558 | 2+ | 10LBR60AA002XB03 | J0202-03 | 辅汽至小机B供汽关断阀故障AUXILIARYSTEAMTOBFPTBCUTOFFVALVEFAULT | SCS | S | DI | NO |  |  |  |  | 18 | 9
586 | 2 | 10LBS40AA202XB01 | J0202-03 | 4段抽汽逆止阀2已开NO.4EXTRACTIONSTEAMCHECKVALVE2OPENED | SCS | S | DI | NO |  |  |  |  | 18 | 10
587 | 2+ | 10LBS40AA202XB02 | J0202-03 | 4段抽汽逆止阀2已关NO.4EXTRACTIONSTEAMCHECKVALVE2CLOSED | SCS | S | DI | NO |  |  |  |  | 18 | 11
588 | 2+ | 10LBS40AA202XB03 | J0202-03 | 4段抽汽逆止阀2故障NO.4EXTRACTIONSTEAMCHECKVALVE2FAULT | SCS | S | DI | NO |  |  |  |  | 18 | 12
1105 | 2 | 10MAL10AA432XB01 | J0202-07 | 高压主调阀2后导汽管疏水阀已开DRAINVALVEFORSTEAMPIPEAFTERCV2OPENED | SCS | S | DI | NO |  |  |  |  | 18 | 13
1106 | 2+ | 10MAL10AA432XB02 | J0202-07 | 高压主调阀2后导汽管疏水阀已关DRAINVALVEFORSTEAMPIPEAFTERCV2CLOSED | SCS | S | DI | NO |  |  |  |  | 18 | 14
1107 | 2+ | 10MAL10AA432XB03 | J0202-07 | 高压主调阀2后导汽管疏水阀故障DRAINVALVEFORSTEAMPIPEAFTERCV2FAULT | SCS | S | DI | NO |  |  |  |  | 18 | 15
1109 | 3 | 10MAL10AA433XB01 | J0202-07 | 高压主调阀3后导汽管疏水阀已开DRAINVALVEFORSTEAMPIPEAFTERCV3OPENED | SCS | S | DI | NO |  |  |  |  | 19 | 1
1110 | 3+ | 10MAL10AA433XB02 | J0202-07 | 高压主调阀3后导汽管疏水阀已关DRAINVALVEFORSTEAMPIPEAFTERCV3CLOSED | SCS | S | DI | NO |  |  |  |  | 19 | 2
1111 | 3+ | 10MAL10AA433XB03 | J0202-07 | 高压主调阀3后导汽管疏水阀故障DRAINVALVEFORSTEAMPIPEAFTERCV3FAULT | SCS | S | DI | NO |  |  |  |  | 19 | 3
119 |  | 10LBC10CL007 | J0202-01 | 高排逆止阀后疏水罐4液位高高THEDRAINVESSEL4LEVELHIGHHIGHAFTERHPCYLINDEREXHAUSTEDSTEAMCHECKVALVE | SCS | S | DI | NO | mm |  |  |  | 19 | 4
118 |  | 10LBC10CL006 | J0202-01 | 高排逆止阀后疏水罐3液位高THEDRAINVESSEL3LEVELHIGHAFTERHPCYLINDEREXHAUSTEDSTEAMCHECKVALVE | SCS | S | DI | NO | mm |  |  |  | 19 | 5
117 |  | 10LBC10CL005 | J0202-01 | 高排逆止阀后疏水罐3液位高高THEDRAINVESSEL3LEVELHIGHHIGHAFTERHPCYLINDEREXHAUSTEDSTEAMCHECKVALVE | SCS | S | DI | NO | mm |  |  |  | 19 | 6
465 |  | 10LBQ20CL001 | J0202-03 | 2段抽汽逆止阀前疏水罐液位高高NO.2EXTRACTIONSTEAMCHECKVALVEFRONTDRAINPOTLEVELHH | SCS | S | DI | NO | mm |  |  |  | 19 | 7
468 |  | 10LBQ20CL004 | J0202-03 | 2段抽汽关断阀后疏水罐液位高NO.2EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINPOTLEVELH | SCS | S | DI | NO | mm |  |  |  | 19 | 8
467 |  | 10LBQ20CL003 | J0202-03 | 2段抽汽关断阀后疏水罐液位高高NO.2EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINPOTLEVELHH | SCS | S | DI | NO | mm |  |  |  | 19 | 9
466 |  | 10LBQ20CL002 | J0202-03 | 2段抽汽逆止阀前疏水罐液位高NO.2EXTRACTIONSTEAMCHECKVALVEFRONTDRAINPOTLEVELH | SCS | S | DI | NO | mm |  |  |  | 19 | 10
1000 |  | 10LCA80AP001XB02 | J0202-05 | 停止/冷渣器冷却水增压泵AASHCOOLERCOOLINGWATERBOOSTPUMPASTOPPED | SCS | S | DI | NO |  |  |  |  | 19 | 11
11 | 1 | 10LBA11AA401YB02 | J0202-01 | 关高压缸左侧进汽疏水阀HPCYLINDERLEFTSIDEINLETSTEAMDRAINVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 0 | 1
61 | 1 | 10LBB31AA401YB02 | J0202-01 | 关中压缸左侧进汽疏水阀IPCYLINDERLEFTSIDEINLETSTEAMDRAINVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 0 | 2
139 | 1 | 10LBC11AA201YB01 | J0202-01 | 开左侧高排逆止阀LEFTSIDEHPCYLINDEREXHAUSTEDSTEAMCHECKVALVEOPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 0 | 3
433 | 1 | 10LBQ10AA411YB02 | J0202-03 | 关1段抽汽关断阀后疏水阀1NO.1EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVE1CLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 0 | 4
538 | 1 | 10LBR40AA441YB02 | J0202-03 | 关小机A进汽母管疏水阀BFPTAINLETSTEAMHEADERPIPEDRAINVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 0 | 5
555 | 1 | 10LBR60AA001YB01 | J0202-03 | 开辅汽至小机A供汽关断阀AUXILIARYSTEAMTOBFPTACUTOFFVALVEOPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 0 | 6
585 | 1 | 10LBS40AA201YB01 | J0202-03 | 开4段抽汽逆止阀1NO.4EXTRACTIONSTEAMCHECKVALVE1OPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 0 | 7
605 | 1 | 10LBS40AA416YB02 | J0202-03 | 关4段抽汽关断阀后疏水阀1NO.4EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVE1CLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 0 | 8
1104 | 1 | 10MAL10AA431YB02 | J0202-07 | 关高压主调阀1后导汽管疏水阀DRAINVALVEFORSTEAMPIPEAFTERCV1CLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 0 | 9
27 |  | 10LBA40AA001YB02 | J0202-01 | 关汽缸加热夹层进汽箱进口电动门STEAMCOLLECTORFORCASINGSANDWITHHEATINGINLETMV.CLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 0 | 10
26 |  | 10LBA40AA001YB01 | J0202-01 | 开汽缸加热夹层进汽箱进口电动门STEAMCOLLECTORFORCASINGSANDWITHHEATINGINLETMV.OPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 0 | 11
4 |  | 10LBA10AA401YB02 | J0202-01 | 关高压缸进汽疏水阀HPCYLINDERINLETSTEAMDRAINVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 0 | 12
108 |  | 10LBC10AA415YB02 | J0202-01 | 关高排逆止阀后#5疏水罐疏水阀THEDRAINVALVEFORNo.5DRAINVESSELAFTERHPEXHAUSTEDSTEAMCHECKVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 0 | 13
104 |  | 10LBC10AA413YB02 | J0202-01 | 关高排逆止阀后#4疏水罐疏水阀THEDRAINVALVEFORNo.4DRAINVESSELAFTERHPEXHAUSTEDSTEAMCHECKVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 0 | 14
100 |  | 10LBC10AA411YB02 | J0202-01 | 关高排逆止阀后#3疏水罐疏水阀THEDRAINVALVEFORNo.3DRAINVESSELAFTERHPEXHAUSTEDSTEAMCHECKVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 0 | 15
18 | 2 | 10LBA12AA401YB02 | J0202-01 | 关高压缸右侧进汽疏水阀HPCYLINDERRIGHTSIDEINLETSTEAMDRAINVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 1 | 1
68 | 2 | 10LBB32AA401YB02 | J0202-01 | 关中压缸右侧进汽疏水阀IPCYLINDERRIGHTSIDEINLETSTEAMDRAINVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 1 | 2
145 | 2 | 10LBC12AA201YB01 | J0202-01 | 开右侧高排逆止阀RIGHTSIDEHPCYLINDEREXHAUSTEDSTEAMCHECKVALVEOPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 1 | 3
437 | 2 | 10LBQ10AA432YB02 | J0202-03 | 关1段抽汽关断阀后疏水阀2NO.1EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVE2CLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 1 | 4
542 | 2 | 10LBR40AA451YB02 | J0202-03 | 关小机B进汽母管疏水阀BFPTBINLETSTEAMHEADERPIPEDRAINVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 1 | 5
559 | 2 | 10LBR60AA002YB01 | J0202-03 | 开辅汽至小机B供汽关断阀AUXILIARYSTEAMTOBFPTBCUTOFFVALVEOPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 1 | 6
589 | 2 | 10LBS40AA202YB01 | J0202-03 | 开4段抽汽逆止阀2NO.4EXTRACTIONSTEAMCHECKVALVE2OPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 1 | 7
609 | 2 | 10LBS40AA421YB02 | J0202-03 | 关4段抽汽关断阀后疏水阀3NO.4EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVE3CLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 1 | 8
1108 | 2 | 10MAL10AA432YB02 | J0202-07 | 关高压主调阀2后导汽管疏水阀DRAINVALVEFORSTEAMPIPEAFTERCV2CLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 1 | 9
96 |  | 10LBC10AA407YB02 | J0202-01 | 关高排逆止阀后#1疏水罐疏水阀THEDRAINVALVEFORNo.1DRAINVESSELAFTERHPEXHAUSTEDSTEAMCHECKVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 1 | 10
92 |  | 10LBC10AA405YB02 | J0202-01 | 关高排逆止阀后#2疏水罐疏水阀THEDRAINVALVEFORNo.2DRAINVESSELAFTERHPEXHAUSTEDSTEAMCHECKVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 1 | 11
88 |  | 10LBC10AA403YB02 | J0202-01 | 关左侧高排逆止阀前疏水阀DRAINVALVEBEFORELEFTSIDEHPCYLINDEREXHAUSTEDSTEAMCHECKVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 1 | 12
84 |  | 10LBC10AA401YB02 | J0202-01 | 关右侧高排逆止阀前疏水阀DRAINVALVEBEFORERIGHTSIDEHPCYLINDEREXHAUSTEDSTEAMCHECKVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 1 | 13
75 |  | 10LBB40AA401YB02 | J0202-01 | 关低旁前疏水阀DRAINVALVEBEFORELPBYPASSCLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 1 | 14
56 |  | 10LBB20AA401YB02 | J0202-01 | 关热再热蒸汽疏水阀HOTREHEATSTEAMDRAINVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 1 | 15
1112 | 3 | 10MAL10AA433YB02 | J0202-07 | 关高压主调阀3后导汽管疏水阀DRAINVALVEFORSTEAMPIPEAFTERCV3CLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 2 | 1
45 |  | 10LBA40AA402YB02 | J0202-01 | 关汽缸加热夹层进汽箱疏水电动门STEAMCOLLECTORFORCASINGSANDWITHHEATINGDRAINWATERMV.CLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 2 | 2
44 |  | 10LBA40AA402YB01 | J0202-01 | 开汽缸加热夹层进汽箱疏水电动门STEAMCOLLECTORFORCASINGSANDWITHHEATINGDRAINWATERMV.OPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 2 | 3
39 |  | 10LBA40AA011YB02 | J0202-01 | 关高压内外缸夹层进汽电动门2DOUBLELAYEROFHPCASINGINLETMV2CLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 2 | 4
38 |  | 10LBA40AA011YB01 | J0202-01 | 开高压内外缸夹层进汽电动门2DOUBLELAYEROFHPCASINGINLETMV2OPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 2 | 5
33 |  | 10LBA40AA010YB02 | J0202-01 | 关高压内外缸夹层进汽电动门1DOUBLELAYEROFHPCASINGINLETMV1CLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 2 | 6
32 |  | 10LBA40AA010YB01 | J0202-01 | 开高压内外缸夹层进汽电动门1DOUBLELAYEROFHPCASINGINLETMV1OPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 2 | 7
456 |  | 10LBQ20AA201YB01 | J0202-03 | 开2段抽汽逆止阀NO.2EXTRACTIONSTEAMCHECKVALVEOPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 2 | 8
452 |  | 10LBQ20AA001YB02 | J0202-03 | 关2段抽汽关断阀NO.2EXTRACTIONSTEAMCUTOFFVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 2 | 9
451 |  | 10LBQ20AA001YB01 | J0202-03 | 开2段抽汽关断阀NO.2EXTRACTIONSTEAMCUTOFFVALVEOPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 2 | 10
429 |  | 10LBQ10AA401YB02 | J0202-03 | 关1段抽汽逆止阀前疏水阀NO.1EXTRACTIONSTEAMCHECKVALVEFRONTDRAINVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 2 | 11
425 |  | 10LBQ10AA201YB01 | J0202-03 | 开1段抽汽逆止阀NO.1EXTRACTIONSTEAMCHECKVALVEOPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 2 | 12
421 |  | 10LBQ10AA001YB02 | J0202-03 | 关1段抽汽关断阀NO.1EXTRACTIONSTEAMCUTOFFVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 2 | 13
420 |  | 10LBQ10AA001YB01 | J0202-03 | 开1段抽汽关断阀NO.1EXTRACTIONSTEAMCUTOFFVALVEOPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 2 | 14
413 |  | 10LBG60AA401YB02 | J0202-03 | 关辅汽至小机A供汽母管疏水阀AUXILIARYSTEAMTOBFPTURBINEAHEADERPIPEDRAINVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 2 | 15
159 |  | 10LBG23AA002YB02 | J0202-01 | 关汽轮机预暖管道电动节流阀MOTORISOLATEDVALVEFORPRE-WARMINGTURBINECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 3 | 1
158 |  | 10LBG23AA002YB01 | J0202-01 | 开汽轮机预暖管道电动节流阀MOTORISOLATEDVALVEFORPRE-WARMINGTURBINEOPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 3 | 2
153 |  | 10LBG23AA001YB02 | J0202-01 | 关汽轮机预暖管道电动节流阀MOTORTHROTTLEVALVEFORPRE-WARMINGTURBINECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 3 | 3
152 |  | 10LBG23AA001YB01 | J0202-01 | 开汽轮机预暖管道电动节流阀MOTORTHROTTLEVALVEFORPRE-WARMINGTURBINEOPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 3 | 4
112 |  | 10LBC10AA425YB01 | J0202-01 | 关VV阀前疏水阀DRAINVALVEBEFOREVVVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 3 | 5
534 |  | 10LBR40AA431YB02 | J0202-03 | 关4段抽汽至小机供汽母管疏水阀NO.4EXTRACTIONSTEAMTOBFPTURBINESHEADERPIPEDRAINVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 3 | 6
530 |  | 10LBR40AA021YB02 | J0202-03 | 关4段抽汽至小机B供汽关断阀NO.4EXTRACTIONSTEAMTOBFPTBCUTOFFVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 3 | 7
529 |  | 10LBR40AA021YB01 | J0202-03 | 开4段抽汽至小机B供汽关断阀NO.4EXTRACTIONSTEAMTOBFPTBCUTOFFVALVEOPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 3 | 8
524 |  | 10LBR40AA011YB02 | J0202-03 | 关4段抽汽至小机A供汽关断阀NO.4EXTRACTIONSTEAMTOBFPTACUTOFFVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 3 | 9
523 |  | 10LBR40AA011YB01 | J0202-03 | 开4段抽汽至小机A供汽关断阀NO.4EXTRACTIONSTEAMTOBFPTACUTOFFVALVEOPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 3 | 10
518 |  | 10LBR20AA001YB03 | J0202-03 | 停小机B排汽阀BFPTBEXHAUSTSTEAMVALVESTOPCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 3 | 11
517 |  | 10LBR20AA001YB02 | J0202-03 | 关小机B排汽阀BFPTBEXHAUSTSTEAMVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 3 | 12
516 |  | 10LBR20AA001YB01 | J0202-03 | 开小机B排汽阀BFPTBEXHAUSTSTEAMVALVEOPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 3 | 13
510 |  | 10LBR10AA001YB03 | J0202-03 | 停小机A排汽阀BFPTAEXHAUSTSTEAMVALVESTOPCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 3 | 14
509 |  | 10LBR10AA001YB02 | J0202-03 | 关小机A排汽阀BFPTAEXHAUSTSTEAMVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 4 | 1
508 |  | 10LBR10AA001YB01 | J0202-03 | 开小机A排汽阀BFPTAEXHAUSTSTEAMVALVEOPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 4 | 2
494 |  | 10LBQ30AA411YB02 | J0202-03 | 关3段抽汽关断阀后疏水阀NO.3EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 4 | 3
490 |  | 10LBQ30AA401YB02 | J0202-03 | 关3段抽汽逆止阀前疏水阀NO.3EXTRACTIONSTEAMCHECKVALVEFRONTDRAINVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 4 | 4
486 |  | 10LBQ30AA201YB01 | J0202-03 | 开3段抽汽逆止阀NO.3EXTRACTIONSTEAMCHECKVALVEOPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 4 | 5
482 |  | 10LBQ30AA001YB02 | J0202-03 | 关3段抽汽关断阀NO.3EXTRACTIONSTEAMCUTOFFVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 4 | 6
481 |  | 10LBQ30AA001YB01 | J0202-03 | 开3段抽汽关断阀NO.3EXTRACTIONSTEAMCUTOFFVALVEOPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 4 | 7
464 |  | 10LBQ20AA411YB02 | J0202-03 | 关2段抽汽关断阀后疏水阀NO.2EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 4 | 8
460 |  | 10LBQ20AA401YB02 | J0202-03 | 关2段抽汽逆止阀前疏水阀NO.2EXTRACTIONSTEAMCHECKVALVEFRONTDRAINVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 4 | 9
601 |  | 10LBS40AA412YB02 | J0202-03 | 关4段抽汽逆止阀2前疏水阀NO.4EXTRACTIONSTEAMCHECKVALVE2FRONTDRAINVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 4 | 10
597 |  | 10LBS40AA411YB02 | J0202-03 | 关4段抽汽关断阀后疏水阀2NO.4EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVE2CLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 4 | 11
593 |  | 10LBS40AA401YB02 | J0202-03 | 关4段抽汽逆止阀1前疏水阀NO.4EXTRACTIONSTEAMCHECKVALVE1FRONTDRAINVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 4 | 12
581 |  | 10LBS40AA031YB02 | J0202-03 | 关4段抽汽至辅汽关断阀NO.4EXTRACTIONSTEAMTOAUXILIARYSTEAMCUTOFFVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 4 | 13
580 |  | 10LBS40AA031YB01 | J0202-03 | 开4段抽汽至辅汽关断阀NO.4EXTRACTIONSTEAMTOAUXILIARYSTEAMCUTOFFVALVEOPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 4 | 14
575 |  | 10LBS40AA002YB02 | J0202-03 | 关4段抽汽至除氧器关断阀NO.4EXTRACTIONSTEAMTODEAERATORCUTOFFVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 5 | 1
574 |  | 10LBS40AA002YB01 | J0202-03 | 开4段抽汽至除氧器关断阀NO.4EXTRACTIONSTEAMTODEAERATORCUTOFFVALVEOPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 5 | 2
569 |  | 10LBS40AA001YB02 | J0202-03 | 关4段抽汽关断阀NO.4EXTRACTIONSTEAMCUTOFFVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 5 | 3
568 |  | 10LBS40AA001YB01 | J0202-03 | 开4段抽汽关断阀NO.4EXTRACTIONSTEAMCUTOFFVALVEOPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 5 | 4
563 |  | 10LBR60AA403YB02 | J0202-03 | 关辅汽至小机B供汽母管疏水阀AUXILIARYSTEAMTOBFPTURBINEBHEADERPIPEDRAINVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 5 | 5
1100 |  | 10MAL10AA421YB02 | J0202-07 | 关高压主调阀疏水阀DRAINVALVEFORCVCLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 5 | 6
1096 |  | 10MAL10AA411YB02 | J0202-07 | 关高压主汽阀疏水阀DRAINVALVEFORTSVCLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 5 | 7
1084 |  | 10LBW30AA002YB02 | J0202-07 | 关轴封供汽溢流旁路电动门BYPASSMVFORGLANDSEALSYSTEMOVERFLOWSTEAMOPENCOMMANDCLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 5 | 8
1083 |  | 10LBW30AA002YB01 | J0202-07 | 开轴封供汽溢流旁路电动门BYPASSMVFORGLANDSEALSYSTEMOVERFLOWSTEAMOPENCOMMANDOPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 5 | 9
1078 |  | 10LBW21AA001YB02 | J0202-07 | 关冷再至轴封供汽电动门MVFORGLANDSEALSYSTEMSTEAMFROMCOLDREHEATERCLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 5 | 10
1077 |  | 10LBW21AA001YB01 | J0202-07 | 开冷再至轴封供汽电动门MVFORGLANDSEALSYSTEMSTEAMFROMCOLDREHEATEROPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 5 | 11
1069 |  | 10LBW20AA003YB02 | J0202-07 | 关轴封供汽调节阀旁路电动门BYPASSMVFORGLANDSEALSYSTEMSTEAMPCVCLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 5 | 12
1068 |  | 10LBW20AA003YB01 | J0202-07 | 开轴封供汽调节阀旁路电动门BYPASSMVFORGLANDSEALSYSTEMSTEAMPCVOPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 5 | 13
1063 |  | 10LBW20AA002YB02 | J0202-07 | 关轴封供汽调节阀前电动门MVINFRONTOFGLANDSEALSYSTEMSTEAMPCVCLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 5 | 14
1062 |  | 10LBW20AA002YB01 | J0202-07 | 开轴封供汽调节阀前电动门MVINFRONTOFGLANDSEALSYSTEMSTEAMPCVOPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 6 | 1
1047 |  | 10LBG50AA001YB02 | J0202-06 | 关1号机组辅汽至轴封供汽关断阀UNIT1AUXILIARYSTEAMTOGLANDSEALINGSYSTEMCUTOFFVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 6 | 2
1046 |  | 10LBG50AA001YB01 | J0202-06 | 开1号机组辅汽至轴封供汽关断阀UNIT1AUXILIARYSTEAMTOGLANDSEALINGSYSTEMCUTOFFVALVEOPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 6 | 3
1039 |  | 10LBG30AA001YB02 | J0202-06 | 关1号机组辅汽至除氧器关断阀UNIT1AUXILIARYSTEAMTODEAERATORCUTOFFVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 6 | 4
1038 |  | 10LBG30AA001YB01 | J0202-06 | 开1号机组辅汽至除氧器关断阀UNIT1AUXILIARYSTEAMTODEAERATORCUTOFFVALVEOPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 6 | 5
1028 |  | 10LBG11AA001YB01 | J0202-06 | 开1号机组低再至辅汽联箱蒸汽关断阀UNIT1COLDREHEATSTEAMTOAUXILIARYSTEAMHEADERSTEAMCUTOFFVALVEOPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 6 | 6
1020 |  | 10LBG10AA001YB02 | J0202-06 | 关启动锅炉至1号机组辅汽关断阀STARTUPBOILERTOUNIT1AUXILIARYSTEAMHEADERCUTOFFVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 6 | 7
1019 |  | 10LBG10AA001YB01 | J0202-06 | 开启动锅炉至1号机组辅汽关断阀STARTUPBOILERTOUNIT1AUXILIARYSTEAMHEADERCUTOFFVALVEOPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 6 | 8
676 |  | 10LBS60AA431YB02 | J0202-03 | 关6段抽汽逆止阀前疏水阀1NO.6EXTRACTIONSTEAMCHECKVALVEFRONTDRAINVALVE1CLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 6 | 9
672 |  | 10LBS60AA411YB02 | J0202-03 | 关6段抽汽关断阀后疏水阀NO.6EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 6 | 10
668 |  | 10LBS60AA401YB02 | J0202-03 | 关6段抽汽逆止阀前疏水阀2NO.6EXTRACTIONSTEAMCHECKVALVEFRONTDRAINVALVE2CLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 6 | 11
664 |  | 10LBS60AA201YB01 | J0202-03 | 开6段抽汽逆止阀NO.6EXTRACTIONSTEAMCHECKVALVEOPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 6 | 12
660 |  | 10LBS60AA001YB02 | J0202-03 | 关6段抽汽关断阀NO.6EXTRACTIONSTEAMCUTOFFVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 6 | 13
659 |  | 10LBS60AA001YB01 | J0202-03 | 开6段抽汽关断阀NO.6EXTRACTIONSTEAMCUTOFFVALVEOPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 6 | 14
645 |  | 10LBS50AA431YB02 | J0202-03 | 关5段抽汽逆止阀前疏水阀1NO.5EXTRACTIONSTEAMCHECKVALVEFRONTDRAINVALVE1CLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 7 | 1
641 |  | 10LBS50AA411YB02 | J0202-03 | 关5段抽汽关断阀后疏水阀NO.5EXTRACTIONSTEAMCUTOFFVALVEBACKDRAINVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 7 | 2
637 |  | 10LBS50AA401YB02 | J0202-03 | 关5段抽汽逆止阀前疏水阀2NO.5EXTRACTIONSTEAMCHECKVALVEFRONTDRAINVALVE2CLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 7 | 3
633 |  | 10LBS50AA201YB01 | J0202-03 | 开5段抽汽逆止阀NO.5EXTRACTIONSTEAMCHECKVALVEOPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 7 | 4
629 |  | 10LBS50AA001YB02 | J0202-03 | 关5段抽汽关断阀NO.5EXTRACTIONSTEAMCUTOFFVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 7 | 5
628 |  | 10LBS50AA001YB01 | J0202-03 | 开5段抽汽关断阀NO.5EXTRACTIONSTEAMCUTOFFVALVEOPENCOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 7 | 6
1135 |  | 10MAW10AA402YB02 | J0202-07 | 关汽封冷却器紧急疏水阀GLANDSTEAMCONDENSEREMERGENCYDRAINVALVECLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 7 | 7
1124 |  | 10MAL10AA451YB02 | J0202-07 | 关中压进汽阀与中压缸疏水阀DRAINVALVEFORRSVANDIPCYLINDERCLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 7 | 8
1120 |  | 10MAL10AA441YB02 | J0202-07 | 关过桥汽封疏水阀DRAINVALVEFORBRIDGEGLANDSEALINGCLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 7 | 9
1116 |  | 10MAL10AA434YB02 | J0202-07 | 关高压主调阀4后导汽管疏水阀DRAINVALVEFORSTEAMPIPEAFTERCV4CLOSECOMMAND | SCS | C | DO | 230VAC |  |  |  |  | 7 | 10
126 | 1 | 10LBC10CT203 | J0202-01 | 高排逆止阀后疏水罐1疏水温度THEDRAINVESSEL1DRAINWATERTEMP.AFTERHPCYLINDEREXHAUSTEDSTEAMCHECKVALVE | DAS | S | TC | TC_K | ℃ | 0 |  |  | 0 | 1
1127 | 1 | 10MAL10CT203 | J0202-07 | 高压主调阀1后导汽管疏水温度DRAINWATERTEMP.FORSTEAMPIPEAFTERCV1 | DAS | S | TC | TC_K | ℃ | 0 |  |  | 0 | 2
2561 | 1 | 10MAV10CT601 | J0202-50 | 汽机润滑油箱#1电加热器表面温度No.1ELECTRICHEATERSURFACETEMPERATUREFORTURBINELUBRICATIONOILTANK | SCS | S | TC | TC_K | ℃ | 0 |  |  | 0 | 3
2643 | 1 | 10MAY10CT601 | J0202-51 | 汽机EH油箱#1电加热器表面温度No.1ELECTRICHEATERSURFACETEMPERATUREFORTURBINEEHOILTANK | SCS | S | TC | TC_K | ℃ | 0 |  |  | 0 | 4
71 |  | 10LBB32CT601 | J0202-01 | 中压缸右侧进汽温度IPCYLINDERRIGHTSIDEINLETSTEAMTEMP. | DAS | S | TC | TC_K | ℃ | 0 |  |  | 0 | 5
70 |  | 10LBB32CT201 | J0202-01 | 右侧中主汽阀前疏水温度DRAINWATERTEMP.BEFORERIGHTSIDERSV | DAS | S | TC | TC_K | ℃ | 0 |  |  | 0 | 6
64 |  | 10LBB31CT601 | J0202-01 | 中压缸左侧进汽温度IPCYLINDERLEFTSIDEINLETSTEAMTEMP. | DAS | S | TC | TC_K | ℃ | 0 |  |  | 0 | 7
63 |  | 10LBB31CT201 | J0202-01 | 左侧中主汽阀前疏水温度DRAINWATERTEMP.BEFORELEFTSIDERSV | DAS | S | TC | TC_K | ℃ | 0 |  |  | 0 | 8
57 |  | 10LBB20CT201 | J0202-01 | 热再疏水温度HOTREHEATERSTEAMDRAINWATERTEMP. | DAS | S | TC | TC_K | ℃ | 0 |  |  | 0 | 9
51 |  | 10LBA40CT602 | J0202-01 | 汽缸加热夹层进汽箱蒸汽温度STEAMCOLLECTORTEMP.FORCASINGSANDWITHHEATING | DAS | S | TC | TC_K | ℃ | 0 |  |  | 0 | 10
49 |  | 10LBA40CT201 | J0202-01 | 汽缸加热夹层进汽箱疏水温度STEAMCOLLECTORFORCASINGSANDWITHHEATINGDRAINWATERTEMP. | DAS | S | TC | TC_K | ℃ | 0 |  |  | 0 | 11
20 |  | 10LBA12CT201 | J0202-01 | 右侧主汽阀前疏水阀后管壁温度AFTERDRAINVALVEPIPETEMP.BEFORERIGHTMSV | DAS | S | TC | TC_K | ℃ | 0 |  |  | 0 | 12
13 |  | 10LBA11CT201 | J0202-01 | 左侧主汽阀前疏水阀后管壁温度AFTERDRAINVALVEPIPETEMP.BEFORELEFTMSV | DAS | S | TC | TC_K | ℃ | 0 |  |  | 0 | 13
7 |  | 10LBA10CT610 | J0202-01 | 高压缸进汽母管温度HPCYLINDERINLETHEADERSTEAMTEMP. | DAS | S | TC | TC_K | ℃ | 0 |  |  | 0 | 14
6 |  | 10LBA10CT201 | J0202-01 | 主汽疏水温度MAINSTEAMDRAINWATERTEMP. | DAS | S | TC | TC_K | ℃ | 0 |  |  | 0 | 15
127 | 2 | 10LBC10CT204 | J0202-01 | 高排逆止阀后疏水罐2疏水温度THEDRAINVESSEL2DRAINWATERTEMP.AFTERHPCYLINDEREXHAUSTEDSTEAMCHECKVALVE | DAS | S | TC | TC_K | ℃ | 0 |  |  | 1 | 1
1128 | 2 | 10MAL10CT204 | J0202-07 | 高压主调阀2后导汽管疏水温度DRAINWATERTEMP.FORSTEAMPIPEAFTERCV2 | DAS | S | TC | TC_K | ℃ | 0 |  |  | 1 | 2
2562 | 2 | 10MAV10CT602 | J0202-50 | 汽机润滑油箱#2电加热器表面温度No.2ELECTRICHEATERSURFACETEMPERATUREFORTURBINELUBRICATIONOILTANK | SCS | S | TC | TC_K | ℃ | 0 |  |  | 1 | 3
2644 | 2 | 10MAY10CT602 | J0202-51 | 汽机EH油箱#2电加热器表面温度No.2ELECTRICHEATERSURFACETEMPERATUREFORTURBINEEHOILTANK | SCS | S | TC | TC_K | ℃ | 0 |  |  | 1 | 4
1126 |  | 10MAL10CT202 | J0202-07 | 高压主调阀疏水温度DRAINWATERTEMP.FORCV | DAS | S | TC | TC_K | ℃ | 0 |  |  | 1 | 5
1125 |  | 10MAL10CT201 | J0202-07 | 高压主汽阀疏水温度DRAINWATERTEMP.FORTSV | DAS | S | TC | TC_K | ℃ | 0 |  |  | 1 | 6
135 |  | 10LBC10CT603 | J0202-01 | 高压缸排汽温度HPCYLINDEREXHAUSTSTEAMTEMP. | DAS | S | TC | TC_K | ℃ | 0 |  |  | 1 | 7
134 |  | 10LBC10CT602 | J0202-01 | 高排逆止阀后蒸汽管上部蒸汽温度THETOPTEMP.OFTHESTEAMPIPEAFTERHPCYLINDEREXHAUSTEDSTEAMCHECKVALVE | DAS | S | TC | TC_K | ℃ | 0 |  |  | 1 | 8
133 |  | 10LBC10CT601 | J0202-01 | 高排逆止阀后蒸汽管下部蒸汽温度THEBOTTOMTEMP.OFTHESTEAMPIPEAFTERHPCYLINDEREXHAUSTEDSTEAMCHECKVALVE | DAS | S | TC | TC_K | ℃ | 0 |  |  | 1 | 9
132 |  | 10LBC10CT210 | J0202-01 | VV阀疏水温度DRAINVALVEPIPETEMP.FORVVVALVE | DAS | S | TC | TC_K |  |  |  |  | 1 | 10
131 |  | 10LBC10CT208 | J0202-01 | 高压缸排汽管疏水温度HPCYLINDEREXHAUSTPIPEDRAINWATERTEMP. | DAS | S | TC | TC_K | ℃ | 0 |  |  | 1 | 11
130 |  | 10LBC10CT207 | J0202-01 | 高排逆止阀后疏水罐5疏水温度THEDRAINVESSEL5DRAINWATERTEMP.AFTERHPCYLINDEREXHAUSTEDSTEAMCHECKVALVE | DAS | S | TC | TC_K | ℃ | 0 |  |  | 1 | 12
129 |  | 10LBC10CT206 | J0202-01 | 高排逆止阀后疏水罐4疏水温度THEDRAINVESSEL4DRAINWATERTEMP.AFTERHPCYLINDEREXHAUSTEDSTEAMCHECKVALVE | DAS | S | TC | TC_K | ℃ | 0 |  |  | 1 | 13
125 |  | 10LBC10CT202 | J0202-01 | 右侧高排逆止阀前疏水罐疏水温度THEDRAINVESSELDRAINWATERTEMP.BEFOREHPCYLINDEREXHAUSTEDSTEAMRIGHTSIDECHECKVALVE | DAS | S | TC | TC_K | ℃ | 0 |  |  | 1 | 14
124 |  | 10LBC10CT201 | J0202-01 | 左侧高排逆止阀前疏水罐疏水温度THEDRAINVESSELDRAINWATERTEMP.BEFOREHPCYLINDEREXHAUSTEDSTEAMLEFTSIDECHECKVALVE | DAS | S | TC | TC_K | ℃ | 0 |  |  | 1 | 15
128 | 3 | 10LBC10CT205 | J0202-01 | 高排逆止阀后疏水罐3疏水温度THEDRAINVESSEL3DRAINWATERTEMP.AFTERHPCYLINDEREXHAUSTEDSTEAMCHECKVALVE | DAS | S | TC | TC_K | ℃ | 0 |  |  | 2 | 1
1129 | 3 | 10MAL10CT205 | J0202-07 | 高压主调阀3后导汽管疏水温度DRAINWATERTEMP.FORSTEAMPIPEAFTERCV3 | DAS | S | TC | TC_K | ℃ | 0 |  |  | 2 | 2
2563 | 3 | 10MAV10CT603 | J0202-50 | 汽机润滑油箱#3电加热器表面温度No.3ELECTRICHEATERSURFACETEMPERATUREFORTURBINELUBRICATIONOILTANK | SCS | S | TC | TC_K | ℃ | 0 |  |  | 2 | 3
78 |  | 10LBB40CT201 | J0202-01 | 低压旁路前疏水温度DRAINWATERTEMP.BEFORELPBYPASS | DAS | S | TC | TC_K | ℃ | 0 |  |  | 2 | 4
2566 |  | 10MAV10CT606 | J0202-50 | 汽机润滑油箱#6电加热器表面温度No.6ELECTRICHEATERSURFACETEMPERATUREFORTURBINELUBRICATIONOILTANK | SCS | S | TC | TC_K | ℃ | 0 |  |  | 2 | 5
2565 |  | 10MAV10CT605 | J0202-50 | 汽机润滑油箱#5电加热器表面温度No.5ELECTRICHEATERSURFACETEMPERATUREFORTURBINELUBRICATIONOILTANK | SCS | S | TC | TC_K | ℃ | 0 |  |  | 2 | 6
2564 |  | 10MAV10CT604 | J0202-50 | 汽机润滑油箱#4电加热器表面温度No.4ELECTRICHEATERSURFACETEMPERATUREFORTURBINELUBRICATIONOILTANK | SCS | S | TC | TC_K | ℃ | 0 |  |  | 2 | 7
1131 |  | 10MAL10CT207 | J0202-07 | 中压进汽阀与中压缸疏水温度DRAINTEMP.FORRSVANDIPCYLINDER | DAS | S | TC | TC_K | ℃ | 0 |  |  | 2 | 8
1130 |  | 10MAL10CT206 | J0202-07 | 高压主调阀4后导汽管疏水温度DRAINWATERTEMP.FORSTEAMPIPEAFTERCV4 | DAS | S | TC | TC_K | ℃ | 0 |  |  | 2 | 9